## Sheet1
Record_Notes | Classification | Model_Classification | score
7/18/2023 12:14:06 PM Kapeliela, Kelsey -0001 Arrived on site checked in with manager, gained roof access Located pharmacy RTU 23, found that the condenser fan motors wouldn’t turn on during cooling causing the compressor to go off on high head pressure After further diagnosing I found that the fan motors weren’t receiving power, after tracing the wires back I found that the electrical connectors at the contactor and capacitors were loose and not making proper contact Replaced connectors, and tested operation, Return air reading at 83 degrees and supply air reading at 54 degrees, called home office before checking out and zone temperature was 71 degrees on departure Call complete checked out with manager Trevon I did notice the the air filters were dirty, I recommend getting them replaced in the near future(picture in attachments) | Compressors/Motors | Compressors/Motors | 0.99851
Bakery Freezer Door & Strip Curtain Damaged LTA-7 Time in 0700 Time out 1630 7/20/2023 Robert F & Bob E Upon arrival checked into ivr and with mod. Accessed back freezer door with tools. Found door top track with rollers crooked and bolts loose. Strip curtain header ripped off and missing three curtains. Used ladder to remove door from top track and rail. Had to go to part vendor to get new bolts and hardware that were damaged. Removed set screws on both ends of rollers to move inside of track further and square roller assembly to bar. Then installed new bolts and hardware to roller rail. Then reinstalled back into top rail. Used crowbar to lift door on each side to install mounting bolts into door on both sides. Adjusted nuts for proper height and that gaskets seal to jamb properly. Cut bottom damaged anchors in track and rotor hammered track into right position with two new concrete anchors. Then used grinder to cut anchors off of damaged and rusted stay roller. Then rotor hammered new anchors into new stay roller and adjusted to door. Removed damaged strip curtain header and installed new header pieces and installed three new curtains and cut to size. Job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99673
8/1/2023 6:14:01 PM Robak, Anthony -0001 Anthony Robak Checked in with MOD Went to cafe freezer to check temp Temp was at 50 degrees on arrival Checked solenoid and thermostat Both working correctly Evap fan working Waited for roof access and went up to club freezer condensing unit Found condensing unit off on high head pressure safety Restarted unit and monitored pressure Discharge at 400+ after little run time Found condenser dirty Checked condenser fans and found fan 1 spinning slowly (left side) Checked fan capacitor and it was good Fan in need of replacement Removed and replaced condenser fan motor with Fasco part number: 71903482 Cleaned condenser with pump sprayer and condenser cleaning agent Restarted unit and monitored pressures Discharge normal for ambient temp (110) Sight glass full Monitored unit until cafe freezer at 10 degrees and still decreasing Checked out with Adrienne complete | Compressors/Motors | Compressors/Motors | 0.99835
WO/ COMPLETE Return to site needed 2nd tech to move case to acces compressor. Verified restrictions on lines causing to run warm. Picked up 14oz of r290 propane as well new drier filter and fittings. Set on vacuum solder new components and pressurized with new gas. Cleaned up and put cooler back in its original place. Waited for case to reach temp checked out with and service manager. Checked in with service channel evaporator was clear waited for cooler to come down to temp but still not reaching setpoint. Will return to continue diagnosing. | Compressors/Motors | Compressors/Motors | 0.99855
7/21/2023 4:28:59 PM Diaz, Ivan -0001 Call for warm air over produce Checked in with manager Located RTU above produce, RTU 3 Gained roof access, located unit on roof and found in idle mode, located controller and found not calling for cooling, zone at temp Called home office and verified setpoints correct, verified system set for occupied space settings, located sensor and verified reading properly, sensor not mounted correctly secured sensor, verified economized closed and not blowing outside air in, tested cooling at unit and verified working properly Notified manager Job complete | Nuisance Calls | Nuisance Calls | 0.99839
Anthony Robak Checked in with MOD Went to cafe freezer to check temp Temp was at 50 degrees on arrival Checked solenoid and thermostat Both working correctly Evap fan working Waited for roof access and went up to club freezer condensing unit Found condensing unit off on high head pressure safety Restarted unit and monitored pressure Discharge at 400+ after little run time Found condenser dirty Checked condenser fans and found fan 1 spinning slowly (left side) Checked fan capacitor and it was good Fan in need of replacement Removed and replaced condenser fan motor with Fasco part number: 71903482 Cleaned condenser with pump sprayer and condenser cleaning agent Restarted unit and monitored pressures Discharge normal for ambient temp (110) Sight glass full Monitored unit until cafe freezer at 10 degrees and still decreasing Checked out with Adrienne complete | Compressors/Motors | Compressors/Motors | 0.99825
ST:11:30-11:45 Arrived checked in with Bryon Advised this call was completed. 10/9 This work was completed on WO: 231005-0268, and the produce cooler will be done on that work order as well. 10/29 by me and another tech. Call complete on this one Checked out with Andrea. | Nuisance Calls | Nuisance Calls | 0.99839
1030-1400 Called out for rack b comp offline Met with manager Jen Inspected compressor, shut down and pulled oil screen. Cleaned. Got compressor online. F/ u to RR Sentronic oil sensor. Ordered from ARS refrigeration, ETA 7/24 | Compressors/Motors | Compressors/Motors | 0.99854
7/21/2023 2:50:02 PM Guerrero, Roberto -0001 Heat-craft M#BEM0475MS6EMAY09 S#T20J24461 I had arrived to store and check in with the manager then diagnosed the wall freezer A4a it frost around the evaporator then I turn on the compressor.then got lift to wash the coil and remove the ice build and curtains was bend so let hot in then I adjusted the curtains and the cement floor has a holes where hot air goes in the wall freezer and put on defrost the heater are working this work order is complete.7/21/23 | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
7/27/2023 Hernandez, Cynthia -0001 The 3 rooms upstairs (office, quiet room, meeting room) are too hot. Needs to be cooler. Checked in with Veronica/Kelly. Went upstairs and each room felt hot. Went up to roof to RTU 20. Suction at 155 psi and discharge at 323 psi. Verified compressor running, cfm running, and blower. Belt looks good. TXV feeding. Economizer closed. Found filters plugged. Removed. Checked other filters on units while walking back to roof hatch. Filters plugged. Was asked to check receiving office AC. Went to e2 to verify status for RTU 20. Went to RTU 13. Suction at 145 psi and discharge 319 psi. Verified compressor running, cfm running, and blower. Belt looks good. TXV feeding. Economizer closed. Found filters plugged. Removed. Went to each room. And each room felt cooler. Called home office informed Marugerite of issues. She changed setpoint to 72 for both. And verified “occupied” status for both RTUs. Informed Nicole and Christian to call filter company to replace all filters for each RTU. Job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99731
Arrived on site and checked in, went to hearing center to look at ac that wasn’t cooling. Found no ac connected to that room. Traced back duct work that was close by by there was nothing that suggested that room has ever had an ac in it. I explained this to manager and suggested that we could put a quote in to install a small portable unit. Manager said to hold off and they would speak to their facility manager to see what they wanted to do. Job completed | Nuisance Calls | Nuisance Calls | 0.99821
8/1/23 JA TT-0800-0930 ST-0930 ET-1300 Little Giant Pump Part #553240 Model-N/A Serial-N/A Call was to replace water pump that was bad -Prior to arrival, drove to United Refrigeration to pick up water pump that has been ordered -Picked up part and drove on site -Upon arrival, checked in with MOD Carlos -Went to area where bad water pump was located -Gained access to Scissor lift since water pump can’t be reached by ladder -Drove scissor lift to water pump location -Tech was already on site and spotted with scissor lift -Went up to water pump -Started carefully removing bad water pump -Made sure to remove water pump without any water leaking out of it -Started installing new water pump -Made sure water pump was secure -Plugged in water pump -Waited for water pump to activate when water drains into it -Water drained into water pump and pump started activating -Went back down on scissor lift and returned scissor lift -Checked out with MOD Jason -Call complete | Compressors/Motors | Compressors/Motors | 0.99759
7/24/2023 7:03:34 PM Caraballo, Marcos -0001 Upon arrival checked in with Mod Fernanda Obtain access to rooftop Tire center water coolers Adjusted and cleaned float for unit one Removed excess water that had built up due to loose float Recommended water pad change out after summer Unit two found bad water pump Travel to supply house to pick up new water pump Cleaned and adjusted Loose water float Ran water pressure through water hose to clear out calcium buildup Recommended water pad change out after summer This call is now complete Checked out and obtain signature from store manager Fernanda | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99703
7/26/2023 1:05:26 PM Kurth, William -0001 This call is a duplicate of Customer po#251682749 | Nuisance Calls | Nuisance Calls | 0.99829
7/21/2023 11:20:04 AM SCHUPBACH, DUSTIN -0001 Found walk in Cafe freezer at 37 degrees. gained access to roof and found unit at 450 psi and opening and closing on its high pressure controll. We cleaned out condenser and head pressure still super high. we ended up pulling out 12 oz. of gas and got head pressure down to ambient plus 30. unit now back online and working. the box is now at 10 degrees and dropping. I will leave call open and check on it after the weekend. if everything maintains I will close call out Monday. 8/1/2023 10:30:32 PM SCHUPBACH, DUSTIN -0003 checked on Cafe freezer walk in. Cafe freezer is at 0 degrees. All operations check out. this call is now complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99693
Sams Club#6619-Ontario Systems:CS1B, CS1C CS: 230719-0151 P.O.: 251298531 —————— 7/19/2023 Steve Fierro TT/ST:1430-1700 Time In:1700 Time out:2015 Checked in with MOD Located cases Found ice up on both coils Deiced both cases checked suction pressure it was efficient No alarms Put system into defrost Checked amps on heaters Receiver @20% Checked superheat on cases found superheat @23 degrees Adjusted txv 1/2 turn opened case Case at 23 degrees upon departure Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99854
11:00-16:00 labor Met with mod and discussed issues that pertained to the exhaust fan in the automotive center. The employee working in the shop told me that the store had experienced a recent power outage/surge and the breaker was found tripped off the following morning. He added that they flipped the breaker back to ON position and had attempted to toggle the ON button for the fan but no response. I got the same results. I proceeded to check for power at the toggle ON/OFF box. I found that 430-440v was present and traveling to the fan motor when the ON button is depressed. I next travelled to the roof and removed all covers up until the electrical compartment at the motor. I checked for power at the motor and found 430-440v present at the non-running motor. The motor is bad, and I need to replace it. Power is now removed for safety. After picking up a new motor at Barsco and X2 V belts, I installed the new motor along with new fan belts onto the exhaust vent. After installation was complete, I restored power to the exhaust fan to test operations. Test was good. Normal operation at this time. Job completed | Compressors/Motors | Compressors/Motors | 0.99797
Compressor Lockout -Single 7/29/2023 6:33:27 AM Gary, Raymond -0001 7/29/23 Ray Gary Arrived onsite and checked in with the manager (Andrew) Accessed roof and went to Rack room A I found compressor 2 in oil lockout Before I reset the controller I checked for oil leaks and oil levels on the compressor Those were all fine Fired off the compressor and let it run for a period of time to see if it would trip on oil again It didn’t trip So I called Sams Monitoring and spoke with (Ietta)She verified all was good THIS JOB IS COMPLETED ALL PICTURES UPLOADED ON MOBILE TECH | Compressors/Motors | Compressors/Motors | 0.99863
8/11/2023 8:59:04 AM Bonner, John -0001 DAIRY WIC Water leak Checked in with manager Anthony on arrival . Call placed for water leak in dairy WIC. Checked WIC and found no signs of water leak. Ran system through defrost and ensured no water was dripping / leaking. Spoke with manager Anthony and they are un aware of any water leak calls placed . No other issues found Job complete | Nuisance Calls | Nuisance Calls | 0.99841
7/17/2023 6:42:40 PM Hines, Marvin -0001 7/17/23 Upon arrival checked in with manager: maryah Tech checked break room airflow/ No airflow Tech gained access to rooftop Tech located : RTU 1. / RTU 16 both not working Tech checked contactors / No 24volts Tech cleaned both condenser coils with water Tech checked all safety switches Tech checked for bad connections Tech reset hi pressure switches Tech gauge up to compressors and checked pressure Tech checked blower motor/ Belt broke Tech installed new blower motor belt on unit Tech has both :RTU working and making temperature Tech checked out with manager : Maryah Make : Lennox Model No. LGE060HH1G Serial No. 5602M04982 Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99695
Travel 1830 Time in 1930 Time out 2000 Checked in with MOD and got roof access. Located frozen door LTA A1A and found case at -3. Checked surrounding cases all running at similar temps. Checked controller on roof and saw no alarms for case and graph looked normal. Called home office to see if they had anything different, no difference found. Checked out with MOD. | Nuisance Calls | Nuisance Calls | 0.99833
En Route: 1845 Time In: 1945 Time Out: 2200 Rack B Multi-Compressor Lockout (Home Office Call) Issues: Gained access to Rack B and the condenser was running on arrival. All compressors offline, in HDP L/O Comp 4 L/O would not reset. Pressures @ 70/260 on arrival Work Done: Reset all compressors. All came online except Comp B4. Called Novar and they could not access the rack, because it was in comm loss. Unplugged the ES1 for 15 minutes and plugged it back in. Alarms finally cleared and Comp B4 came back online. Suction pressure dropped down to 32 psi, set point @ 35. Monitored rack for awhile to ensure no further issues. All cases at temp. Job Complete | Compressors/Motors | Compressors/Motors | 0.99852
Arrived on site checked in with manager and service channel. Located LTA05 bakery freezer . All evap fans running and no ice build up on coil . Called home office temp in walk in freezer is at 0 . Setpoint it at -2 . It reached setpoint serval times today . Walk in door was left open causing high temps . No further issues . Job complete 1130-1200 travel OT 1200-1300 labor OT | Nuisance Calls | Nuisance Calls | 0.99841
Tech notes from SVC: Created By Kenneth Dias PMC Southwest Work Summary: Arrived at site at Rack A compressor a4 replace oil float and pump and did 3 acid tests on all racks WM | Compressors/Motors | Compressors/Motors | 0.99849
On-site 1930-2300 Arrived on site. Checked in with manager. Made way to MTB15 for rotisserie prep room Temp sitting at 50° Evap coil was frozen up One of the fans was not running Found it disconnected from plug, reconnected and fan turned on Deiced coil Monitored prep room and dropped to 40° Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99835
7/30/2023 8:28:35 PM Alcaraz, Jose -0001 TT 2000-2100 Time in 2100 Time out 2230 Follow up Arrived log into service channel and check in with manager for multiple cases high temp -check rack found B6 a,b in alarm -no other alarms -found cases B6 a,b ice up -had product pulled -the store is closing soon and there is no over night crew -turn cases off to deice over night -follow up for tomorrow to turn cases back on and diagnose 7/31/2023 10:41:46 AM Maldonado, Chris -0002 Start time-0915 End time-1245 complete logged into service channel checked in with manager Vivian took case B06A and B apart to make sure not iced up drain is cleared called sporlan waited for a call back never called me back called Sams teach support to check set point and defrost time B06A set point-22 degrees and it’s at 30 degrees Defrost times-6 times a day termination 35 min or 47 degrees B06b set point-22 degrees and at 30 degrees Defrost times-was set at one time a day termination time at 35 min and 47 degrees had Sams teach support changed to 6 times a day to match B06A checked out with manager Vivian and explained to her why it iced up | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
8/3/2023 2:06:01 PM Hernandez, Cynthia -0002 The HVAC tech we had in today advised we get all our ac filters changed out because they are dirty. She mentioned 48 filters total for the building Checked in with Kelly. Got roof access. Checked all units. Found filters dated 07-28-23 by another 3rd party. Job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99716
08/2/23 EDLT WIF A4.2 and A5.2 Checked in with mod upon arrival My Corrigo isn’t loading up having issues with my app or data Went to freezer temps were at 8 and 9 on both the freezers walked inside the freezer everything was running no ice build up all fans were running Checked pressures all were good to Liquid level was good Watched the freezer for awhile and seen temps drop and go back up when people would open the doors and back door Checked graph logs and matched it to see if it would drop to temps and they do when the store is closed The temps will rise back up when they stock up and let the doors close Freezer usually takes a while to drop back down but the store opens and due to the amount of people that open the doors the temps will rise and drop Informed mod about it Complete | Nuisance Calls | Nuisance Calls | 0.99808
Replaced guied for track on bottom of door on pos freezer .. checked to insure working n f correctly all ok . | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99682
Cooper Nichols 9/22/22 Arrival 1500 Depart 1515 Duplicate call Completed already Reference call # 230920-0297 | Nuisance Calls | Nuisance Calls | 0.99827
Incomplete, parts on order. Tech inspected fans in meat prep room that was making “loud noises”. Tech turned fans off, removed fan covers to inspect and make sure nothing is interfering with fans, tech saw nothing interfering the fans. Tech found source of “loud noise”. Tech deemed that fan motor was wearing out and will need to be replaced as soon as possible or fan will continue to make loud noise and need to be replaced soon. Model number of motor: F2208A3955S Serial: 15092200076 Tech has parts in hand, tech checked on fan to make it was still running and temp is holding, everything is normal. Tech will return following Monday to replace fan motor | Compressors/Motors | Compressors/Motors | 0.99794
Returned removed pos door and removed gaskets and bad hearts. Replaced with new also when removing electrical found that tripped a braker unable to find do to employees wanted to leave will have to return to find missing leg of power. Rehung door. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9971
7/18/2023 David Rivera checked in found the door . Had condensate took door off checked voltage it was good. Cleaned the prongs and the door installed it back on . The door needs to be replaced the heaters are going out. Will send info to Willie to order parts. Job incomplete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9966
Jul 27, 2023 Found a wire short near light toggle switch and in an abandoned electrical whip. Went through wiring and got rid of the electrical whip that was arcing out. Labeled the breakers with the appropriate case systems, labeled them fans and lights. Put case back together and got all case and shelf lights on. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99706
7/30/2023 Morales, Angel -0001 Checked in with mod. Notice evaporator txv panel open causing to heaters to not work properly and cause strainers to start building ice. De iced strainers and txv ice build up. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
Arrived onsite checked the vfd for any faults pulled graphs found the sub cooler not working and the sporlan controller frozen reset power to control and reprogrammed the controller checked operation and sub cooler everything’s working properly Call completed | Capital Replacement | Capital Replacement | 0.97794
8/13/2023 3:31:28 PM Smith, Stephen -0001 EnRoute: 13:25 Time In: 13:50 Time Out: 16:50 LTA-01 -1 LTA-02 1 LTA-03 2 LTA-04 defrost Arrived and checked in with manager, made my way back to the freezer and found A04 running warmer than the rest of the others. Verified all fans were running and no ice build up on coils, went to rack and checked receiver level and if sight glass was flashing. Sight glass was solid and receiver level was fine. Did find compressor 3 was off on temperature control, I reset the switch and comp 3 started running. Went to check condenser 1 motor not running. Will pick up motor from parts house and return on follow up to replace, part should be local. Temperatures for A01-3 started dropping they are running at -1 to 2 degrees while A04 is in defrost. Ran everything I found through team lead. Checked out with Raymond Jerek 9/20/2023 9:35:54 AM Smith, Stephen -0003 EnRoute: 8:00 Time In: 10:00 Time Out: 11:15 Rack A Arrived on site and checked in with Service Channel. Climbed on top of rack and found all condenser fans to be running. Checked rack B and C and all fans were running as well. Got with the team to see who changed it and found out David changed it on separate ticket. Call is complete | Compressors/Motors | Compressors/Motors | 0.99855
7/25/2023 9:33:19 PM Porrata, Favian -0001 Upon arrival checked in with Manager Peter. Call was for no water in the tire center swamp cooler. Started off by access swamp cooler. Started to do my inspection and found the swamp cooler to be on but water to be off. Made sure pump was good. Than check to make sure water float was also good. Than found the water line to be shut off. Turned water line back on and swamp cooler back on. Swap cooler is now cooling. Notice float is old and not stop at full line will need to replace. Will return to install part. Call incomplete. 7/26/2023 4:35:17 PM Porrata, Favian -0002 Upon arrival checked in with Manager Peter. Call was for follow up and install new float in swamp cooler. Had to wait to get roof access. Once got access to roof started off by powering down unit. Turn water line off. Took apart old float. Installed new float in to system. Made sure to level float correctly. Turn water back on to check for any leaks. No water leaks. Turned unit back on. Call complete. | Capital Replacement | Capital Replacement | 0.98849
Brandon Cox Arrival 1045 Departure 1315 Notified manager(Peter) was here to check on the damaged coil. Found RTU 14 with coil fixed due to micro leaks in coil. Got a plastic bag and electric tape Covered coil to prevent from tripping high head pressure. Need to quote to replace coil. Need a crane 35 feet up and 30 feet in. Also need 410A recovered Coil changed out. Charge system back up and check ops. Call not complete. | Capital Replacement | Capital Replacement | 0.9793
Make: KYSOR/Warren Model: TD600-073-VL-4-FHSRX-A Serial: 1112000167 Unit: Rack A comp#4 -upon arrival compressor was off but the rack at suction set point. -I checked the compressor and the oil level was low. The reason for the low oil level is that the OLC needed to be adjusted. -I monitored system and OLC is satisfied and oil level was restored. No other issues system operational. | Compressors/Motors | Compressors/Motors | 0.99838
Travel 1430-1500 Labor 1500-1630 Travel from 1630-1745 Checked in with MOD Removed water from drain pan Diagnosed faulty drain pan heater New drain pan assembly expedited ETA Monday 08/14/23 Follow up needed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99838
AGE 08/30 CANNOT CHARGE 7/19/2023 8:41:19 AM Gary, Raymond -0001 7/19/23 Ray Gary Arrived onsite and checked in with the manager (Paul)I walked every case that was supposedly alarming I found all the temperature were fine So I checked air flow and that was good I advised Paul that I found no problems I took pictures of each case tag and temp readings and uploaded them on mobile tech THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99818
7/28/2023 5:13:06 PM Lopez, Miguel -0001 Incomplete, Parts on order. Checked in on site. Located walk-in needing services. Used ladder to disconnect fan & remove fan cover. Fan adjusted to minimize noise, cover re-installed. measured walk-in curtains and filled form and sent to willie to order parts. 8/24/2023 4:37:54 PM Young, Roderick -0002 Job Complete Had to pick up parts for this job Arrived on site and replaced all of Strip Curtains in the Bakery Cooler. Job also required a fan motor replacement in the Bakery cooler but it seems to be working fine | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99487
LTA 8 Bakery FRZ Arrived to site checked in with mod On-site for bakery WIF high temp On arrival freezer at 25-30F Found coils frosted up due to roll seal door not closing Ran a defrost cycle on freezer to remove all ice and clear coils Verified heaters are operating and fans are shutting off in defrost Ice build up issue is door being stuck open Cleared coils and pulled door down to maintain freezer temp (Door repair on another WO that I will address after this WO) Freezer down to temp and out of alarm On-site for multiple tickets Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
7/17/2023 Bob E and Robert On arrival tech check in with service channel and store manager. Was showed problem with produce roll up door. Talked with manager Claudia will return tomorrow 5:00 am to do repairs. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99655
DAIRY WIC Water leak Checked in with manager Anthony on arrival . Call placed for water leak in dairy WIC. Checked WIC and found no signs of water leak. Ran system through defrost and ensured no water was dripping / leaking. Spoke with manager Anthony and they are un aware of any water leak calls placed . No other issues found Job complete | Nuisance Calls | Nuisance Calls | 0.9984
7/23/23 TH TT: 17300-18:15 Time in: 18:15 Time out: 20:00 C1 and C3: Dairy CLR Air Curtain HRC incorporated SN: 21-AL002 Checked in with Service channel and MOD(Karla). Went to Rack C. Condenser Coil is clean. Suction and Discharge pressure at set point. Liquid level is good and full sight glass. Checked the location. Found the Air curtain wasn’t strong and Found the Supply side grill was dirty. Found the Supply duct bend blew to unit C3 and C1 side. Cleaned the dust inside the supply grill. Bend the supply to Return grill. Adjusted the inverter to make a Supply air strong. Checked the temperature are good temp and keep going down. Cleaned the work area. Informed and checked out with MOD(Karla) and Service channel. Job finished | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99665
7/18/2023 3:24:12 PM Bustillos, Andrew -0001 -Arrived on site checked in with MOD -located dairy walk in -Found that coil had frost and built up ice on C2b -when going into defrost water would drop on the floor -Proceeded to put C2b into defrost -Cleared ice with hot water making sure coil was free of all frost and ice -Noticed drain had blockage preventing proper flow of water to drain -cleared drain pipes making sure water flowed through properly. -after clearing drain and removing ice from coil made sure no other evaporators in dairy had ice build up -No other issues found -All fans in dairy working properly and running at proper temp -call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99866
7/22/2023 2:12:43 PM DiCecco, John -0004 RTU 3 LCB060HN2G 5602E02629 Arrived and investigated newly installed compressor. Found terminals to be destroyed and insulation to be grounded with megohm meter. Recovered charge and removed compressor. Replaced filter drier. Pressure tested system and evacuated. Charged with 12# of 407C. Monitored system operation and noted high suction pressure due to 95 return temp. Will return later in the week to verify pressures and ops. Amp draws stable and within range. Call incomplete. 7/22/2023 4:24:32 PM Devlin, Joseph -0005 Assisted Jake with compressor replacement. 7/23/2023 12:29:56 AM Warden, Cody Assisted tech on site with compressor swap. Installled TXV and Filter Dryer. 7/24/2023 7:13:18 AM Martinez, Alexis -0001 Hvac unit : Cafe Brand: Lennox Model:LCB060HN2G Serial:5602E02629 Original Compressor: Model: ZR57K3E -TFD-830 Checked in with mod Rob Checked our with mod Vanessa and Irene Reason for call: Cafe running warm. Issue found: compressor grounded. Resolution: replacedcompressor, TXV, Filter Drier, and add new refrigerant R407c will need to follow up finish call. Checked in with mod Rob and informed him that roof access was needed Roof hatch was unlocked and proceed to cafe unit Upon inspection of unit found it not running Checked disconnect -Good Flipped the breaker on and heard the indoor blower motor turn on After 10 mins the compressor contactor kicked on and immediately tripped the breaker Proceeded to check resistance on the compressor Found that compressor was grounded Spoke with mod about getting replacement Mod approved Proceeded to call supply shops Found compressor and proceeded to gather materials needed for compressor change out Contacted The crane company for crane truck Crane truck said they will send one to our location Proceeded to Supply shop to gather materials Crane did not arrive on scheduled time and informed us they will not be able to make Canceled crane and proceeded to lift compressor on to roof top along with tools and materials that were needed removed previous compressor, filter drier and TXV. Added new compressor filter drier and the supply shop had sent wrong TXV -proceeded to supply shop to pick up the correct TXV and proceeded back to job site Added acid away to compressor Pressure tested And held nitrogen Vacuumed until 420 microns Could not finish installation due to rain and wind headed our way. Will follow up on call Saturday July 22. 7/24/2023 6:53:10 PM Decarlo, Anthony -0003 Let tech borrow torch rig 8/7/2023 8:11:47 AM DiCecco, John -0006 Checkin Checkout RTU 3 LCB060HN2G 5602E02629 Asset #003881 Arrived and inspected compressor health. Found pressures favorable and amp draw within range. Call complete. | Compressors/Motors | Compressors/Motors | 0.99851
Checked in with manager tiger and inspected case MTC 19 and it was at temp from the previous body they had de-iced the case and it is now running at temp 30F. Inspected cooler and saw it was iced up and set it to a defrost and de-iced the coils. Coil is now de-iced and running at temp. The coils iced up because of intermittent power failures caused the rack to go down and the controllers to glitch and while refrigeration was valves on the fans were not running and it cause incomplete defrosts. The rack was brought back up, but the controllers were glitched. Reset the controllers and after the defrosts the cases and the produce cooler got back down to temp. KRACK MODEL # GND56A-340TDB-STP WT ST ST ST SERIAL # MY21C020840 Let the manager know that the produce cooler was at temp and running normally and that the controllers are running normally. Let the manager know to have an electrician inspect the health of the electrical power coming in to the store as intermittent power failures are common at this store. Checked out with manager silva Call Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
7/21/23 Sams 6614 230721-0266 251517319 1445-1800 Working with tech Robert F. We repaired the Meat cooler door see his notes for details | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99692
7/25/2023 6:15:06 AM Brooks, Byron -0001 Travel: 0845 Time in: 1030 Time out: 1430 checked in with MOD Located produce walk in cooler Produce cooler has no roll down door Used ladder to access top of unit Took picture of serial number Sent information in to get roll down door ordered Spoke with manager about roll down door Chrscked iut with MOD F/U when part comes in to be 9/20/2023 12:00:13 PM Jahantabi, Saman -0003 Incomplete Check with manager We prepare everything for inspection Manager stopped installing presses because they don’t want to close produce for 2 hours We will back tomorrow after 8 PM 9/21/2023 10:47:56 PM Jahantabi, Saman -0005 Complete Checked with manager Located produce walk in cooler Installed new one 9/22/2023 8:24:02 AM Brooks, Byron -0004 Travel: 1900 Time in: 2000 Time out: 0030 checked in with mod Located produce walk in cooler Grabbed new produce walk in door Accessed scissor lift Removed old door Used scissor lift to hoist new door up Put in new door and chain hoist Got door functioning properly and produce walk in cooler now has door Checked out with mod Call complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99735
08/18/23 EDLT A4.1 FREEZER DOOR HANDLE Checked in with mod and service channel Located freezer A4.1 Found the door handle and it wasn’t broken everything was right on it Noticed the bolts on the bracket for the door handle were loose and making the door handle not stay in place Also made the door harder to open since it wasn’t balancing the handle Tightened the bolts on the bracket and tested the handle and worked smooth the handle will not need to be replaced Complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99562
8/15/2023 6:10:40 PM Cho, Yoonhyun -0001 DESCRIPTION: INCOMPLETE! Found the AC unit, RTU-7, IAQ on the roof. The compressor #3, and #4, working fine. The compressor #2 was not working. Required for compressor #2, then it works. There was a small leak from the high side service port. Tightened the Schrader valve core. Will change gas to compressor #2 tomorrow. 8/17/2023 7:49:25 PM Cho, Yoonhyun -0002 DESCRIPTION: The job was completed. Checked in with the manager Francisco. The restaurant level of the compressor #1 was very low. I saw the leaking area with the sign of oil splash on the compressor mounting place. Performed gas leak detection on evaporator coil, expansion valves, condenser coils, and compressors. There was a small leak on the high side service port, and tightened the Schrader valve core, and replaced the old caps with new ones for the service ports. Sealed the caps with thread sealant. Charged the 14 lbs of R410A from my truck stock. All the four compressors are working properly. The AC RTU 7 drains much condensation water properly. The job was completed. | Compressors/Motors | Compressors/Motors | 0.99754
7/20/2023 4:02:15 PM Alvarado, Christopher -0001 Checked in with manager located cafe freezer operating. Freezer is at -5 must of been a duplicate Wo I worked on this freezer 2 days ago under another Wo. | Nuisance Calls | Nuisance Calls | 0.99817
7/14/2023 7:06:19 PM Lawson, Christopher -0001 Completed Checked in with manger on site went to rack c found compressor 2 off reset high pressure switch compressor came straight on then inspected compressor checked oil rack was full on oil and compressor was too then called Digital asset an made sure it was running good they said it was good no other issue found 7/15/2023 10:41:48 AM Moran, Greg -0002 Checked out freezer and question. Found ice everywhere. Ran system through defrost deiced with torch blew out drain line found plugged with dirt trash cleaned up ice. | Compressors/Motors | Compressors/Motors | 0.99857
Arrived on site checked in with the manager mentioned the beverage case by the cafe not working -hussmann model #ID5SM6 serial #MY19B012280 case #B14 -found the evaporator iced up -went up to the roof to the condensing unit and after troubleshoot found the defrost timer bad and not turning automatically -drove to a local part shop and got a defrosted timer -went back to site and installed the defrost time and the unit start to go to defrost -de iced the evaporator -manager said after we got power outage this happened -the defrost shorted because of the power outage -all checked good and the temperature dropped normally -call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
Assisted Rodrigo with compressor replacement. | Compressors/Motors | Compressors/Motors | 0.99853
7/31/2023 12:49:32 PM Schrock, Kevin -0001 Checked in with manager and checked operation of rack B comm. Found comm loss on multiple cases. Located beginning comm port and reset module. Monitored operation and all cases now communicating normally. | Compressors/Motors | Compressors/Motors | 0.99806
Marcos Caraballo 07-24-23 Travel 1130 Arrival 1200 Departure 1700 Upon arrival checked in with Mod Fernanda Obtain access to rooftop Tire center water coolers Adjusted and cleaned float for unit one Removed excess water that had built up due to loose float Recommended water pad change out after summer Unit two found bad water pump Travel to supply house to pick up new water pump Cleaned and adjusted Loose water float Ran water pressure through water hose to clear out calcium buildup Recommended water pad change out after summer This call is now complete Checked out and obtain signature from store manager Fernanda | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99689
Both lights work tried on another case.Something’s wrong inside case and needs to be looked at by a refrigeration tech I have no way to check a ballast | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99704
7/29/2023 12:28:10 PM Hunter, Garrett -0001 7/29/23 Garrett Hunter Lta 7 running warm Upon arrival checked in with Mgr and service channel, went to bakery freezer found door switch had been knocked off the wall, causing solenoid to de energize, happened yesterday at some point, had another tech pull up graph for Temp history, repaired problem by moving the switch and resetting the actuation point, now when door is completely closed door no longer hits box of switch, watched box drop in temp checked out with mgr Claudia call complete | Damage by Customer | Damage by Customer | 0.98378
7/26/2023 10:01:51 AM Rodriguez, Johnson -0001 The manager was asked and alarms were verified and everything working was identified. the manager has no idea about this call. | Nuisance Calls | Nuisance Calls | 0.99812
Nobody knew what this call was about and cases are at temp. Completing out. | Nuisance Calls | Nuisance Calls | 0.99817
8/5/2023 4:58:56 AM Gary, Raymond -0001 8/4/23 Ray Gary Arrived onsite and checked in with the manager (Corey)Found the case not refrigerating The fans were on So I went thru my diagnostics and found the liquid line ball valve was closed off On Monday I believe I went and defrosted that whole case So I know it was working fine and the ball valve was in the open position There is construction going on so someone from that side my have actually shut the valve off I let the case temp out for a while and Called Sams Monitoring and spoke with (Ietta)She confirmed the case was out of alarm and working properly THIS JOB IS COMPLETED | Damage by Customer | Damage by Customer | 0.98436
Condenser A Checked in with store manager Rebekah Access motor room and check condenser A operations Control by VFD condenser fan motor number two seized and condenser coil plugged pump down both racks toggle off compressors and power off condensers removed fan guards and wash condensers coils from top and bottom assemble and restarted Located replacement CFM and picked up Remove and replace condenser fan motor number two Pulling 1.7 amps per leg all condenser fan motors online suction pressure 14 psi discharge pressure 260 psi R404A Job complete | Compressors/Motors | Compressors/Motors | 0.99854
8/17/2023 4:07:44 PM Cosgrove, Reese -0001 On-site 1000-1545 Arrived on site. Checked in with manager. Made way to roof to check rackE comp1. Comp1 was in high pressure lockout. Reset and compressor is operational. Found one condenser fan motor not running Checked fuses and fuses are good Checked power to contactor and power was present Removed fan guard and checked electrical wiring on motor Found disconnected wire. Repaired wiring and cycled power back to the motor Condenser fan motor is operational and all are running at this time Checked pressures on rack. Suction @ 38psi Discharge @ 289psi A few evap coils are slightly high temping Found 2 coils iced up in the produce cooler Used scissor lift for access Deiced evap coils in produce cooler Monitored temps to ensure they dropped All cases are now at temp All condenser fan motors are operational Receiver level is at 35% All checks okay at this time Job complete | Compressors/Motors | Compressors/Motors | 0.9985
This compressor is being replaced today on another work order . | Compressors/Motors | Compressors/Motors | 0.99783
Helped another tech replace glass door. We adjusted the torque rod. Door is now opening and closing properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99726
7/28/2023 10:06:29 PM Lawson, Christopher -0001 Completed Checked in with manger on site went to cafe case was told water was lecking from sides so went behind case and took bottom panel off. Found drain stopped up sohad them pulled product in case to get to drain waited about 30 mins then seen sitting water in case so blow out drain with co2 3/4 times then noticed more water on floor. Went behind case and noticed floor drain wasnt draining so tryd to clean up some of the stuff in drain. Told manger gip going to need a plumber out for the floor drain but case is draining good now now other issues | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
8/10/2023 6:51:05 PM Hanamornsate, Thirathanawat -0001 8/10/23 TH TT: 17:00-18:15 Time in: 18:15 Time out: 20:15 LTA1 & LTA2: Rollseal Door MN: RS-500 Track KIT SN: 0009113 Checked in with Service channel and MOD. Checked the location. Found the Rollseal Door blanket was tangled. Unlock the Motor brake. Management the Door blanket to position. Put the Motor brake to position. Called Manual mode for now because this Rollseal Door needed to be replace and New Door is already order and waiting for shipping to store soon. Checked Door operation open and close. It’s working good on manual mode. Cleaned work area. Checked temperature all 4 cases. Temperature at 1a, 1b and 1b showed 12 Degrees F and 2b showed 16 degrees F. They still going down to setting point. Needed to be close the Door longer for kick them out of alarm but the Employees needed to be open it for pickup product inside. Checked all graph temperature were good before the Door had stuck opened. It should be kick out of alarm high temp in this night. Informed and checked out with MOD and Service channel. Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99714
8/3/2023 9:10:35 PM Maldonado, Chris -0001 Start time-1530 End time-2200 complete checked in with manager Michael Hooper asked manager to move product leaking from LTA-6 broke up ice on the floor and dumped it out side broke up ice in drain pan plastic in drain pan, cleared drain with co2 test drain with gal of water replaced old drain pan with new drain pan (Jose will email Sheena and Sarah on Aug-4-23 for price of drain pan) put case in defrost to make sure heaters work (all hearts working) de-ice coil and txv cleaned up water and ice from floor and shelves checked out with manager Michael Hooper 8/4/2023 4:52:15 AM Brooks, Byron -0002 Travel: 1345 Time in: 1800 Time out: 2145 drove to shop. Picked up drain pan Drove to sams club Checked in with MOD Unwired drain heaters Assisted tech in changing out drain pan for MTB-9 Cleaned all ice Cleared drain pipe Rewired heaters Reassembled unit De-iced rest of ice in unit Turned unit unit into defrost and it was working correctly Drain pan clear and drain pipe Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99847
08/07/2023-Glenn Sr. Bob and Robert Upon arrival checked in with manager and Service Channel. Proceeded to cooler with loose and broken safety poles. Assisted Bob on removing poles. Filled up broken concrete with epoxy and reinstalled safety poles. See Bobs notes | Damage by Customer | Damage by Customer | 0.96821
Start time-2200 End time-2230 complete checked in with manager Raymond hayden arrive to dairy cooler MITB-5 ° MTB-6° at set point 31 degrees called home office to confirm (MITB-5 ° MTB-6° running at set point) checked out manager Raymond hayden | Nuisance Calls | Nuisance Calls | 0.99831
8/1/2023 9:46:16 AM Maldonado, Chris -0001 Start time-1030 End time-1145 complete checked in with Oscar went to ice cream case A10A to check temps all temps are good (-8,-6,-4) came out of defrost home office call called walmart home office to check defrost schedule and set point temps set point10 defrost schedule-termination at 55 degrees or 45min. 1 defrost per day checked out with manager Oscar | Nuisance Calls | Nuisance Calls | 0.99838
8/5/2023 5:11:11 PM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Ashton. MOD Ashton showed me all the case is running on negative temperature. Meat SD cooler MTA 6.3 6.4 6.5 MTA 7.1 A B C MTA 7.2 A B C MTA 8.1 A B C MTA 8.2 A B C MTA 8.3 A B C -Went to Rack house and all compressors are online. Receiver level at 20% and no alarm. Notice the Rack monitor is offline -Called Sam’s Club HO and Rack A is in loss comm -Restore communication. Called Sam’s Club HO and Rack A is back in communication -Checked each case for air flow and found MTA 6.3 no air flow. Removed all panels and de iced the coil using trash can and water pump -Monitor all case and it reached target temperature of 22f. None of the case went down to negative temperature -Run defrost to all case and temperature reached set point and controller turned off the refrigeration -Locate manager and talked to MOD Veronica. Showed her all the cases that are holding the temperature desired -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99825
8/3/2023 4:31:33 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke with the manager Alfred. I looked at A2 compressor and found that the breaker is tripped. I turned breaker off and checked through the electrical and found a burnt wire in electrical box on top of the compressor. It looks like the overload is fried so I will order a new overload. I spoke to Alfred and told him I will leave this work order open. 9/7/2023 1:11:18 PM Brandau, Kenneth -0002 Drove to United and picked up new module. Arrived at the store, logged into Service Channel and spoke with the manager, Alfred. I removed the existing bi metal overload. That was fried. Re did the wiring, added new wires, installed the new hybrid module. Compressor is working properly now. This is complete no need for follow up. | Compressors/Motors | Compressors/Motors | 0.99852
10/24/2023 5:38:14 PM Bankhead, Ventrice -0001 Sams 8177 -Checked in with manager upon arrival. -Located case listed on work order. Found no ice build up, management advised the work order had been completed a couple weeks ago. They stated that they had a walk in freezer leaking water. Ltb5b was leaking water onto floor due to condensation pan missing screw and hanging. -Remounted pan and inserted screw. -Pan no longer leaking. -Call complete | Nuisance Calls | Nuisance Calls | 0.99835
7/19/2023 8:18:27 PM Fierro, Steve -0001 Sams Club#6619-Ontario Systems:CS1B, CS1C CS: 230719-0151 P.O.: 251298531 —————— 7/19/2023 Steve Fierro Checked in with MOD Located cases Found ice up on both coils Deiced both cases checked suction pressure it was efficient No alarms Put system into defrost Checked amps on heaters Receiver @20% Checked superheat on cases found superheat @23 degrees Adjusted txv 1/2 turn opened case Case at 23 degrees upon departure Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
Checked in with Mark Let him know I was here to check on the dairy walk in cooler. We walked over to check it out, saw that some of the evaporators in there were icing up. Told him we would need a lift to get up there and deice them and check if the drain plug is clogged. He told me I won’t be able to get a scissor lift in there right not since customers are walking in there. He said if we could come back when they close. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99822
Completed. Checked in with management. Checked controller and found temperatures reading approximately zero. Checked freezer and found no issues. The door must have been open for a long period of time. Found ice on fan guards. Removed ice and cleaned the area. | Nuisance Calls | Nuisance Calls | 0.99831
Chad Dodge Arrival OT 1200 Departure 1300 Arrived at store found door latch not set right causing door to stay open and high temp Adjusted latch so door will close | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99705
7/20/2023 6:26:46 PM Stuart, Christopher -0001 Compressor L/O alarm(s) cleared and are back online. We were on-site for the Heat Reclaim change-out and had to close off some valves to isolate the water tanks, which caused the compressors to trippin on oil L/O No issues. Call complete | Capital Replacement | Capital Replacement | 0.98385
7/25/2023 7:39:08 AM Bonner, John -0001 Rack B Kysor warren Model -TD430-098-SC-4-FXSRGBI Serial -0305001075 Checked in with manager kris on arrival. Call placed for compressor L/O on rack B. Went to rack house and checked ops. Found rack B maintaining suction at 55# Found all compressors online / no compressors found locked out . All systems are down to temp / no active alarms. Called home office and spoke with Zach. Ensured no alarms on there end and confessors are online. Job complete | Nuisance Calls | Nuisance Calls | 0.99778
alarms and systems were checked and everything was found working. | Nuisance Calls | Nuisance Calls | 0.99825
8/7/23 Ray Gary Arrived onsite and checked in with the manager Went to The rack house a Found the receiver around 12 percent Because of the alarm I did a visual and electronic leak search Found nothing to raise my concerns So I went to the cases and did an electronic leak search on each case Got no hits I called Sams Monitoring and spoke with Carlos And he said it wasn’t in alarm any more THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99804
Arrived at site at LTB 3 case fans were not running checked power going into case had power checked electrical Clixon was not on the line re installed it and fans came back on waited for temp to reach set point Case is in temp | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99702
Arrived on site and checked in with David. Started assisting with with the lights on the walk in cooler. Started walking around the store looking for a ballast for the lighting system. Unable to find one in the case near the doors. Got scissor lift out and checked the top of the cooler and unable to find anything up there as well. Walked around and found all electrical panels in multiple locations. No ballast found. Checked the rack house and no ballast found. Started tested the voltage for the lights and found 120 at the top of cooler junction box and at the junction box inside the cooler found no voltage. Electrician needed. Updated manager Noel. Cleaned up and checked out with Noel. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99697
7/17/2023 6:22:37 PM Rodriguez, Mateo -0001 Arrived on site and checked in with manager Sandra Was told by an employee that someone from another company was just here working on prep table and they’re ordering gaskets for the unit. Spoke to manager and she wasn’t aware of someone else working on it. She told me to not check it out Checked out with manager Liliana | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99468
7/26/2023 7:17:29 AM Ried, Nicholas -0001 Completed. Checked in with management. Used scissor lift to access the evaporators in the meat walk-in. Found drain pans dry but cleared lines anyway. The evaps did have condensation. Wiped off all water. The condensation is mostly due the fact that there are no strip curtains on the main door allowing moisture into the cooler. Management has already placed an order for new curtains and hardware. Unable to use Service Channel to close ticket. Confirmation number 658424316 | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99662
Time in: 1515 Time out: 1645 located case BS-2 Temp reading 38 Product blocking means of service Removed product Found product had bent back pant onto coil reducing airflow Shut off refrigerant valve Case has good airflow Both fans are working properly Used water to de-ice coil Plugged fans back in Turned refrigerant valve back on Reassembled case Checked out with MOD call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99705
Aug 21, 2023 Forced defrost, found screw missing from back of drain pan had dropped down. Bent up, replaced screw, and let defrost. No water is dripping. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99826
8/23/2023 5:39:58 AM Delgado, Jesus -0001 Spoke with manager. Monique was told case maintain temperature throughout day called home office verify temperature log use probe to verify correct temperature on case AS10 Case is maintaining setpoint all at normal at this time this call is complete. | Nuisance Calls | Nuisance Calls | 0.99824
Start time-0845 End time-0930 complete check in with manager Kenny checked cafe cooler temp running above 70 degrees checked breaker, and coils to make sure not cooler. (No issue) got roof access located MTRCU1 shut off on high head cleaned coils and raise psi from 350 to 380 checked temp running at 30 checked out with manager kenny | Nuisance Calls | Nuisance Calls | 0.99507
7-24-23 Paul Z / FU to install ventilation fans checked in with Jeremy picked up parts from supplier house returned and installed fan motors and replaced capacitors on other motors all motors are working at this time job completed | Compressors/Motors | Compressors/Motors | 0.99826
8/10/23 TH TT: 17:00-18:15 Time in: 18:15 Time out: 20:15 LTA1 & LTA2: Rollseal Door MN: RS-500 Track KIT SN: 0009113 Checked in with Service channel and MOD. Checked the location. Found the Rollseal Door blanket was tangled. Unlock the Motor brake. Management the Door blanket to position. Put the Motor brake to position. Called Manual mode for now because this Rollseal Door needed to be replace and New Door is already order and waiting for shipping to store soon. Checked Door operation open and close. It’s working good on manual mode. Cleaned work area. Checked temperature all 4 cases. Temperature at 1a, 1b and 1b showed 12 Degrees F and 2b showed 16 degrees F. They still going down to setting point. Needed to be close the Door longer for kick them out of alarm but the Employees needed to be open it for pickup product inside. Checked all graph temperature were good before the Door had stuck opened. It should be kick out of alarm high temp in this night. Informed and checked out with MOD and Service channel. Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9971
8/23/2023 3:33:18 PM Soto, David -0001 Tire Shop MUA -Arrived on site and checked in with store -found water line cracked on roof for swamp cooler -shut off water and repaired copper line -turned back on and confirmed proper float ops -job complete | Capital Replacement | Capital Replacement | 0.98554
8/29/2023 1:49:56 AM Simon, Devin -0001 Evaporator was ice up. After the defrost process I monitored the temp drop. When alarm cleared, I check case and temps were good. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99802
8/9/2023 2:17:43 PM Calderon, Jose -0001 Checked in with manager Tanya, ordered fans and submitted quote for parts with Lawrence. Let the manager know that the parts are in quote status Checked out with manager Tanya submitted quote Call Complete 8/30/2023 8:51:23 PM Calderon, Jose -0002 Added pictures of the condenser data plate and the rack data plate. 10/3-BILL INCURRED. REPAIR TO BE COMPLETED ON WO 230823-0054. waiting on quote Call Incomplete | Capital Replacement | Capital Replacement | 0.98209
8/1/2023 12:32:35 PM Delgado, Jesus -0001 found faults alarm on compressor 6 rack. Core sense had 2 flash alarm, lock rotor amps Check for voltage at contactor found contactor pitted not allowing all 3 legs to power compressor. Remove failed contactor with auxiliary. Installed new contactor with auxiliary. Check amps on compressor once parts were installed. Check wiring ensure connections are secure. Alarm is clear on compressor. All at normal at this time Parts used Auxiliary contactor call is completed. | Compressors/Motors | Compressors/Motors | 0.99859
Check in with manager Sean on arrival rack a satellite compressor S3 intermittently going into failure due to current sensing relay board not sending correct output voltage remove board and replace with OEM part install then re-address with same address as existing board spoke with Zack from Home Office was told compressor is now showing amp draw and is at normal. | Compressors/Motors | Compressors/Motors | 0.99863
7/29/2023 6:31:56 PM Alcaraz, Jose -0001 TT 1730-1815 Time in 1845 Time out 1930 Call complete Arrived log into service channel and check in with manager for rack A high super heat -found controller in comm loss -reset controller -cases all went down to temp -receiver level at 30% -all fan running on condenser | Nuisance Calls | Nuisance Calls | 0.99812
Arrived at location checked in with manager Jim gained access to roof inspected rack A and verified that it was compressor that has been ordered for replacement system circuit switch is shut off and main power breaker shut off called monitoring and spoke with Carlos who stated he overrode compressor off so that it would not send alarms no further issues at this time. | Compressors/Motors | Compressors/Motors | 0.99857
7/28/23 Ray Gary Arrived onsite and checked in with the manager (Chasity)Went to compressor one and it was running Went thru some checks of my he compressor and found no issues I called Sams monitoring and spoke with(Trina)She verified that the compressor is not in oil Lärm THIS JOB IS COMPLETED | Compressors/Motors | Compressors/Motors | 0.99866
This is not a recall. On a previous call tech came out and diagnosed faulty oil pressure switch, had Sams club order new oil safety switch and part has not been recieved. until new oil safety switchs are installed 8/8/2023 Tobe, Jeffery -0001 Upon arrival located manager to start job, found that several compressors was off on oil safety reset compressors checked oil separator had two balls floating and compressor oil level 3/4 full on all compressor watch temperature drop to the negative digits all ok at this time complete | Compressors/Motors | Compressors/Motors | 0.99861
Arrived on site and checked in with the manager. Went to RTU 14 and replaced the transformer , condenser fan relay and the touch screen. Turned the unit on and addressed the the board. Novar is reading the temperature, went to RTU 13 and replaced the board and the touch screen , addressed the board and it reading on novar. RTU 26 replaced the fuse and it is back online as well. All RTU’s and AHU’s are back on line. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.9966
10/5/2023 10:36:05 AM Zaun, Paul -0001 10-5-23 Paul Z / LTA4B Grocery freezer LTA4B checked in with Jeremy checked WIF LTA found box at 5F checked controller temperature found box was in defrost LTA 5a&5B and LTA 4 A&B are high temperature after defrost circuit timed out monitored temperature LTA 4B & 4A came down in temperature to -2F distribution tubes, orfice and temp sensor was changed checked coil for ice build up -there is no ice on evaporator Job completed | Nuisance Calls | Nuisance Calls | 0.99823
7/21/2023 6:31:20 PM Lopez, Noe -0001 07/21/23 Noe Lopez System: Cafe HVAC RTU 13 -Checked in with MOD -Manager stated cafe is running warm -Went to check controller everything came out good -Called digital assets and verified everything was fine on there end -Went to unit to inspect it -Filter was fine -Cleaned out evaporator had some gunk on it -Condenser coil looked very dirty -No water outlet available -Went to Home Depot to pick up 200ft of water hose (left hoses in room on roof) -Used numerous cycles of water to rinse coils off, large amount of dust and dirt came off -Cleaned out other condenser coils that were next to RTU 13 -Cleaned of drain line as well -Put unit back together -Checked controller everything checked out fine -Upon reviewing the cafe area noticed the heat was coming from pizza oven -Went to inspect exhaust fast, motor was spinning slow -Turned breaker off and on unit was not functioning -Determined motor will have to be replace -Manager put ticket in 251531230 -Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99854
7/31/2023 10:32:54 PM Rudnick, Bryan -0001 This is for Dairy walk-in cooler. Not Produce walk-in. Manager Mark specified that this call is for Dairy and has a different call he’s opening for Produce. On-site, checked in with manager Mark. Proceeded to work on Dairy cooler. Brought scissor lift over and connected hoses. Three coils iced up and leaking. Verified drains were clogged and iced over. Deiced all 3 coils and used nitrogen to clear out drains. Water is properly draining down drains now and no more leaks. Cleaned up everything and Let manager Nimah know the resolution. Dairy cooler C8 Brand: Heatcraft Model: WK270BEC Serial: T20F20531 Refrigerant: R407A C9 Brand: Heatcraft Model: WK270BEC Serial: T20F20535 Refrigerant: R407A C12 Brand: Heatcraft Model: WK270BEC Serial: T20F20533 Refrigerant: R407A Checked out with manager Nimah Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99845
Arrived on site and checked in with manager Nick. Started going over everything asked on service channel. B-13 case high temping at 90°. B-19 case hi temping at 41° and LT-SC IC DRS high temping at 8°F. Started with the LT-SC IC DRS case to make sure product was not in danger. After further investigation, found that there are two cases/circuits that are labeled the same one is under rack B the other one is under rack A. After calling Novar found that rack A circuit controls the RCU unit on top of the roof that controls the actual ice cream doors behind the three main POS freezers and cooler. After further investigation in order to find the second circuit due to nothing being labeled. Finally, after going through the store was able to find that the curb side pick up Freezer is the one labeled under rack B. Labeled the case above the temp controller on case for both cooler and freezer. Case is iced up and getting very little airflow and temping currently at 6°F Case LT-SC IC DRS Self contained Brand -Heatcraft Model -QIV5V14-03AMUN Serial -C16B01356 After diagnosing, the unit found that the condenser was extremely packed and could not have airflow through the coils, causing the refrigerant not to condense properly and causing icing issues on the evaporator coil, due to flood back. Once condenser coil was cleaned properly and blown out with CO2 due to the case, being a self-contained and not being able to deice properly using a hose and water in fear of flooding, spoke with manager and decided to turn off the case while further diagnosing other cases that are temping incorrectly. Opened all the doors removed the panels and allowed Ambient temperature to penetrate case in order to defrost naturally. Let case defrost and checked the heating element operation and the programming based on manufacturing specs and everything was running good just the issue with the condenser being dirty seems to be the only issue with the case. Turned case back on before leaving and running through another defrost cycle and gave the manager the all clear of case is at temp in the morning to start using. Started further diagnosing circuit B-19 case Brand -Heatcraft Model -DX6XN-08RUN Serial -C16A00839 Case has multiple work orders opened under this issue that was quoted for work to be done called Novar and was going over case programming and controls. Found case was completely iced up and had no airflow at all. Started deicing and going over controls and setpoints with novar. After case was deiced started checking valves and superheats after further investigation and checking with previous technicians found that the case needs new TXVs that were already ordered. Making sure defrost and everything was working properly will complete parts install on work order 230801-0310 and TN 252496960. Started going over the B-13 case which is high temping as well at 90°F. B-13 case is the MD Pizza case located in front of the cafe. Case controller upon initial look over is at 29°F which is the setpoint for this case. Started taking apart the case to further diagnose, found that the honeycombs were extremely dirty and needed to be blown out and can cause lack of airflow. Found case was temping properly, but not showing correctly on Novar rack controller for circuit monitoring. Brand -Hussmann Model -?2???6XE Serial -?000162142 Started taking apart panels and tracing temp sensor making sure there’s no disconnect. Case module is reading proper case temperature but monitoring is still reading 90°F. How to take apart drain line and bottom of case in order to access 1081 opus controller. Did not find any issues with sensor or terminal points. Going back-and-forth between electrical room controller back to case found that under rack control monitoring, case sensor is reading properly at 29.7°F but control temp is reading 90°F with sensor fault possible that case control board is bad. Called novar after resetting opus controller and waiting the time for case to reset. Once case reset correct temp came up on the rack monitoring. Made sure case continued to operate correctly and updated manager call is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99864
8/7/2023 6:39:47 PM Clichici, Sorin -0001 08/07/2023 Sorin Clichici True Model # TTP-AT-67-HC Serial # 10169080 Pizzeria Self contained unit Upon Arrival check in with store manager and SCP Gain access to pizzeria found refrigerator overload with products advise personal working there to move on pizzeria cooler Food storage on the bottom of the refrigerator (shelf are not in position) disconnect refrigerator from power supply remove unit front grill ,found condenser very dirty . remove front evaporator panel and evaporator motor fan found iced up evaporator water inside of the pan start to remove ice from drain pan noted drain line clog clear evaporator drain line , remove all ice Tested with water all ok water goes free blow clean the condenser using nitrogen reinstall all parts back clean remove all water accumulated inside of the fridge remove condensate water pan , clean wash and install a set of wicking pads reinstall back both shelves Power on the fridge , cycle well at 31.0F cut out 35.O F cut in Call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
8-10 Scotty Sparks Travel time 1400-1430 On site 1430-1830 Departure 1830 Checked in and out with candy Checked opes on cooler door. Found several doors needed adjusting. Adjusted all POS FREEZERS AND COOLER DOORS as needed. Checked all other doors in store. All ok. Meat door has been hit by forklift. Separate call was placed. Will follow up on Monday 8-14 per manager Ray. This call is completed. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99733
07:30-11:00 (3.5 hours REG) Arrived on site got everything set up for compressor swap, on Rack B. Found out we received the wrong compressor for this call. Took compressor back and ordered the right compressor. New compressor is 6 -8 weeks out. Will return to install when new compressor comes in. | Compressors/Motors | Compressors/Motors | 0.99858
Installed new door gaskets through out the store on the walk in freezers/coolers and adjusted doors. There are still some that need new torque rods, another tech has some on order on another work order. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99722
In 08:00 out 11:30 Checked in with Maryann Working on freezer door not closing properly Checked door and found door is bent damaged by forklift Found door gasket starting to tear will need to be replaced Also found outside door handle damaged and starting to come loose will need to replace Also trim on door is damaged and needs to be replaced Will order all parts and replace The door is pretty damaged and bent is part replacement does not fix problem we may need to replace door follow up required | Damage by Customer | Damage by Customer | 0.98437
Returned and located braker . Also found loose neutral in main electrical box . Made correct now power not cutting in and our. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99715
Checked in with mod. Notice evaporator txv panel open causing to heaters to not work properly and cause strainers to start building ice. De iced strainers and txv ice build up. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
7/18/2023 12:25:09 PM St. Amant, Kenneth -0001 Sam’s club #: 6619 System: compressor B1 SC: 230717-0612 PO: 251183533 —————— 7/18/23 Kenneth St.Amant Travel-06:00-08:00 Onsite-08:00-12:00 Checked in with manager Arrived on site checked in with location gained access. When to motor room and B1 was locked out on oil Checked oil level, oil psi and normal operating Everything is all good Compressor back online and running Checked out with manager Kelly Job complete | Compressors/Motors | Compressors/Motors | 0.9986
8/30/2023 8:15:26 PM Sovran, David -0001 This is a duplicate call. 230820. Notes and time will be put towards that call | Nuisance Calls | Nuisance Calls | 0.99828
7/18/2023 7:52:04 PM Brooks, Byron -0001 Travel: 1800 Time in: 1900 Time out: 2130 checked in with MOD Located LTA-07A oand LTA-07B Cases had airflow Thermostat read cases are at 1 degrees and 2 degrees Product blocking means of service Had product removed Disassembled cases Used hose and hot water to de-ice cases and clear drain pans Plugged fans back in Fans working Reassembled cases Cases had good airflow and went back to temp Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9983
7/16/2023 4:01:06 PM Lopez-Castro, Dylan -0001 Produce MTC-1 Walk in door 07/16/2023 Dylan Lopez Arrived on site checked in and out with manager and service channel went to MTC-1 found door not lined right. Verified with store manager Robert that 2 techs will here at 20:00pm Tuesday night to fix door verified with bob emmer that it’s a non mech issue pics on mobile tec verified with supervisor call incomplete 7/17/2023 5:16:07 PM Emmer, Bob -0002 7/17/2023 Bob E and Robert On arrival tech check in with service channel and store manager. Was showed problem with produce roll up door. Talked with manager Claudia will return tomorrow 5:00 am to do repairs. 7/18/2023 4:46:29 AM Frietze, Robert -0003 Produce MTC-1 Walk in door 7/17/2023 Robert Bob See Bobs notes 7/18/2023 10:35:24 AM Emmer, Bob -0005 7/18/2023 Bob E and Robert On arrival tech check in with service channel and store manager. Helped Robert repair produce roll in door. See Roberts notes and pictures job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99719
TI: 8:00 am TO: 12:15 Helped Dustin diagnose issue with little freezer in sams club break room, discovered pinched wire and a little bit of ice blocking the fan from running, verified that fan motor itself was good and that heater was working, removed ice and made sure unit came down too temp | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99815
TI: 8:30 am TO: 12:00 pm Helped dusting diagnose issue with cooler not coming down too temp, unit had high pressure and was over filled with gas, recovered some of the gas and made sure the unit was running correctly. Checked on cooler in Cafe and made sure it was coming down too temp | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99657
8/8/2023 4:48:07 PM Kaser, Wade -0001 Incomplete, parts on order. Case is missing metal piece that connects top of neighboring case together. Tech took pictures of what is missing from the front, top, and back of case, and also took photo of what is needed to complete this work order. Parts order email has been submitted and will return to complete work order once missing part has arrived. Model #: QLG1-12UN Serial: C17F01350 Type: coffin/bunker 9/25/2023 2:23:14 PM Kaser, Wade -0002 Completed. Received part that needed installation. Located meat case that was missing the piece, case was being stocked at the location of the missing piece. Once stockingu was completed, I removed the black plastic bumper enough to put new piece in, removed tape covering metal piece. Once in place, I lined up the holes to put screws in. Put plastic bumper back in place and made sure metal piece was all the way in place. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99682
TT 0715-0845 On-site 0845-1015 2 door break room ric Sams# 0085211 True M#T-35 S#8695634 Arrived on site and checked in with service channel and manager. Found 2 door ric in break room with both gaskets torn. Called local supply house and located gaskets. Placed on will call for me. Will pick up in am and return to install. Notified manager. Follow up. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99715
7/24/23 Ray Gary Arrived onsite and checked in with the manager (Nick)I found the right side of the evaporator coil slightly iced over So I defrosted the Coil with warm water and made a very slight adjustment to the TXV I checked for any more leaks and cleared the drain with nitrogen and warm water to ensure proper flow No other issues found this job is completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
Sams 6683 Murray 7-21-23 Service call 230721-0343 Po 251528137 LTB Compressor L/O Condenser tripped Job complete Travel 1700-1730 On job 1730-1915 Travel 1915-1945 Found VFD in bypass Checked all fans All fans operational Reset VFD 105° ambient temp Condenser tripped again creating high discharge pressure Condenser tripped again on earth fault #2 Checked motor winding good Checked motor shorts to ground non Found Found rub out on wires going to motor Cut shorted wires out Reconnected Condenser now out of bypass Now at 307psi down from 320 Compressors on order on other work orders No temp issues Checked out with MOD Mike | Compressors/Motors | Compressors/Motors | 0.99855
Check cases found cases sweeting found doors heaters not working repaired connections nowThe working will need to replace 3door. Gasket has be order at Unit houma la | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99728
arrived on location checked in with the receiving manager gained access to the roof top I found the unit not running so I put the unit in test mode and the one stage of cooling works fine so I took it out and ran down stairs to check on the hvac monitor and no units where communicating with the controller so I contacted novar and attempted to reestablish communication with the controller I was able to get a few units to communicate but novar was having issues getting them to consistently communicate I spoke with a couple colleagues and I found Adolfo has parts on order that should help the issues we are finding with the units. I informed the manager of my findings and checked out I will be returning Tomorrow to try and remedy the communication issues call incomplete this call is also related to this tracking number 251682915 | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.9959
Arrived on site at 12:45am -no one on site , ring the bell in the front and the back in the receiving area and no one answered -no cars in the parking lot and no cars in the back where -called the dispatch and said he will push it for tomorrow -calm on follow up | Nuisance Calls | Nuisance Calls | 0.99832
7/25/2023 9:32:48 PM Porrata, Favian -0001 RTU 15 Lenox M#SCA240H4MN1G S#5608G14113 Upon arrival checked in with Manager Peter. Call was for RTU 15 not on. Began by checking if the disconnect was off and it was. Started to do my inspection of the unit. Made sure compressor where good. Than began to check belt and inspected blower wheel. Checked to see if the filters where good and they are. Made sure to check wiring for anything that looked out the ordinary. Everything checked out turned unit back on. Unit is now running and has a 23 degree split. Call complete. | Nuisance Calls | Nuisance Calls | 0.99825
10/9/23 Top off rack Picked up refrigerant needed to preform job upon arrival checked in with store manager gained accsess to rack and topped off with 4 jugs of r422d now recivor level between 35-40 all ok job completed | Compressors/Motors | Compressors/Motors | 0.99855
8/8/2023 4:19:40 PM DeBeaulieau, Andrew -0001 Breaker for compressor 4 on rack A tripped. Checked and found no shorts. Found burn wire on top of contactor. Clipped burnt section and reland wires on contactor. Restarted compressor. Found 108-115v drop across contact points on middle phase. Replaced contactor and auxiliary switch. Compressor back online. Call complete. | Compressors/Motors | Compressors/Motors | 0.99867
7/17/2023 7:24:44 PM Hanamornsate, Thirathanawat -0001 7/17/23 TH Time in: 20:45 Time out: 21:00 Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643 Arrived on site and checked in with Service channel and MOD(Justin). This called is duplicated the PO#251141303. Informed and checked out with MOD(Justin) and Service channel Job finished | Nuisance Calls | Nuisance Calls | 0.99844
Inspected fan covers. Ordered 4 new fan covers. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99747
7/20/2023 7:01:59 PM Boesch, Jonathan -0001 Gp# 230720-0348 Time in 1630 Time out 2000 Hussmann M# F-8G S# MY21D037223 Checked in with manager George Located bunker case running warm at 38. Inspected it and found the coil was completely iced over. Contacted Sams EMS and requested manual defrost of the unit. Used sump pump, hot water, garden hose to defrost the coil completely. Once all the ice was removed, placed unit back into service. Defrost heaters and all fans are working properly. Coil superheat is normal. Unit is running normally at this time. Checked out with manager George. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99869
8/18/2023 5:06:35 PM De La Torre, Emilio -0001 08/18/23 EDLT A4.1 FREEZER DOOR HANDLE Checked in with mod and service channel Located freezer A4.1 Found the door handle and it wasn’t broken everything was right on it Noticed the bolts on the bracket for the door handle were loose and making the door handle not stay in place Also made the door harder to open since it wasn’t balancing the handle Tightened the bolts on the bracket and tested the handle and worked smooth the handle will not need to be replaced Complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99615
Arrived at location, checked in with manager Shana. Got access to rack b. Proceeded to work on rack b. Verified that there is no alarms present. Checked alarms a day ago and compressor 3 starts alarm on 7/23. Checked alarms 7 days ago and compressor 3 and compressor 4 oil/lock out. Verified compressor 3 and compressor 4 contactors are getting proper voltages from L1-L2 472v, L1-L3 472v, L2-L3 473v, amp draws compressor 3 L1 21.22, L2 22.14, 21.64, amp draws compressor 4 L1 28.40, L2 28.82, L3 30.78. Compressor 3 oil pressure is at 55psi, compressor 4 oil pressure is at 60psi. Suction pressure is at 28.3psi-setpoint 36 psi. Suction temp 50 degrees and drop leg is 93 degrees. Discharge pressure is 225.7psi and setpoint 200.20psi. Transducer pressure is at 225psi witch is matching the discharge pressure. Transducer on suction was at 35 psi matching with suction pressure. Condenser fans are all running. All compressors have the proper oil level in them. The receiver oil level is at one ball. Refrigerant receiver level is at 50% and site glass is full. Did a efficiency pump down test on all compressors and nothing is pulling backwards on pressures and pumped down accurately. Found one dip Switch on board that was put into on mode and switched it back to auto mode. Called Novar and spoke with April. Asked how many times has the alarm occurred in the past. Only alarm was from yesterday and that everything looks good ever since yesterday into today and all cases are temping properly. No issues found. Let manager Chris know the resolution. MTB rack Brand: Hill Phoenix Model: PS425SMRAD Serial: 25417-129 Refrigerant: R404A 1300Ibs Asset tag: 0007893 Checked out with manager Chris Call complete | Compressors/Motors | Compressors/Motors | 0.99862
TT:7:00-10:00 ST:10:00-12:15 Arrived checked in with manager Suman Gained roof access made way to rack c upon arrival found two compressors tripped on high head. Discharge pressure was at 322 upon arrival. Found that 4 out of 8 CFMs not running. Checked VFD and it’s in bypass currently. Checked high voltages at all contactors for the CFMs all getting 481v to each contactor. And getting 124v to the coil. All good Checked fuses for the contactors found two of them motors bad used fuses from the other two motors to get those up and running. Found two motors bad and they where ordered and are at the shop spoke with Jim and we will be replacing next week. After getting two fans back on and running and VFD bypassed discharge pressure is at 216.1psi and suction pressure is at 28.6 Rack C: MODEL TD400 -050 -SC -4 -OHDQ-C REFRIGERANT-R404A SERIAL NO. 0603000645 Call complete will complete repairs on other ticket. Checked out with club manager Kristan | Compressors/Motors | Compressors/Motors | 0.99822
Jul 20, 2023 Checked grab n go case, it was high temping. Checked over solenoids, heater, and wires. Found RTU 3 off, the wires were not right and was loose. Reattached wires to main power source and connected wires into contactor. Unit started up and case dropped in temp. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99659
8/4/2023 10:29:01 AM Gonzalez, Alan -0001 Checked in with Mark Let him know I was here to check on the dairy walk in cooler. We walked over to check it out, saw that some of the evaporators in there were icing up. Told him we would need a lift to get up there and deice them and check if the drain plug is clogged. He told me I won’t be able to get a scissor lift in there right not since customers are walking in there. He said if we could come back when they close. 9/8/2023 5:15:08 PM Gonzalez, Alan -0002 Deice dairy cooler Checked in with Mark Let him know we were here to deice the evaporators in the dairy coolers units C8-C13. Asked if we could have some of the pallets moved from the middle of the cooler. He said he will send someone to move them for us. Got the scissor lift and moved them in the dairy cooler. Went to my van and got my trash can and sump pump with hoses. Set up the hoses and went to get hot water in my trash can. Once everything was set up we checked each evaporator to see which ones needed to be Deiced. Evaporator C8, C9 and C12 had ice on both sides of the unit. Started by deicing unit C12 first, as we were spraying water on the coils there was water dripping on the floor so we went to get a big container so the water would fall in there. As water fell in the container some would still splash on the floor so we went to get a mop and bucket. As one of us sprayed water in the ice the other one would mop up the water that would get on the floor so customers would t slip with the water. Once done with that unit we moved over to C8 and did the same thing. Unit C9 was the worse one with a lot of ice on both sides. As we Deiced the evaporators we had to keep going for more hot water so we can clear out all of the ice. After melting all of the ice we moved out the scissor lift and cleaned up all of the puddled water on the floor. Cleaned up the area and took our equipment back to the van. Checked out with Mark Let him know what we did. Job complete 9/9/2023 1:36:06 PM Enciso, Juan -0003 Assisted Alan on this call , we began to bringing all the stuff in with the scissor lift , after we had everything in place we then grabbed hot water , brought it to the walk-in and began spraying hot water . We got big buckets under the coils to prevent flooding the walk-in , there was water dropping into the floor so I grabbed a mob and began moping while Alan was de icing coil. After everything was completed and de iced we then mopped the whole walk-in where the water splashed. Walk-in got cleaned . Took everything back together and it’s place and checked out with mark. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
Rack Associated: MTB Alarm Message: Suction Pressure Manual Comment: Two compressors are locked out and high suction pressure at 64 psig HOME OFFICE ONLY Refrigeration -HO Use Only Rack House Compressor Repair Raised By: Ruben Borges Contact: mod Position: mod Scheduled date: July 24, 20232:18 PM 7/25/2023 12:20:07 PM Rudnick, Bryan -0001 Arrived at location, checked in with manager Shana. Got access to rack b. Proceeded to work on rack b. Verified that there is no alarms present. Checked alarms a day ago and compressor 3 starts alarm on 7/23. Checked alarms 7 days ago and compressor 3 and compressor 4 oil/lock out. Verified compressor 3 and compressor 4 contactors are getting proper voltages from L1-L2 472v, L1-L3 472v, L2-L3 473v, amp draws compressor 3 L1 21.22, L2 22.14, 21.64, amp draws compressor 4 L1 28.40, L2 28.82, L3 30.78. Compressor 3 oil pressure is at 55psi, compressor 4 oil pressure is at 60psi. Suction pressure is at 28.3psi-setpoint 36 psi. Suction temp 50 degrees and drop leg is 93 degrees. Discharge pressure is 225.7psi and setpoint 200.20psi. Transducer pressure is at 225psi witch is matching the discharge pressure. Transducer on suction was at 35 psi matching with suction pressure. Condenser fans are all running. All compressors have the proper oil level in them. The receiver oil level is at one ball. Refrigerant receiver level is at 50% and site glass is full. Did a efficiency pump down test on all compressors and nothing is pulling backwards on pressures and pumped down accurately. Found one dip Switch on board that was put into on mode and switched it back to auto mode. Called Novar and spoke with April. Asked how many times has the alarm occurred in the past. Only alarm was from yesterday and that everything looks good ever since yesterday into today and all cases are temping properly. No issues found. Let manager Chris know the resolution. MTB rack Brand: Hill Phoenix Model: PS425SMRAD Serial: 25417-129 Refrigerant: R404A 1300Ibs Asset tag: 0007893 Checked out with manager Chris Call complete | Compressors/Motors | Compressors/Motors | 0.99863
7/27/2023 4:38:49 PM Denison, Carter -0001 Time in 1445 Checked in with manager Stated coil leaking in walk in cooler MTB-2 Coil MTB-1a iced up Deiced coil so it could drain properly Cleaned up residual water with a rag from bottom of coil Talked with manager and maintenance will clean up water on floor of cooler with floor machine Checked out with manager V | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
Arrived on site, checked in with management. There was a rain, thunderstorm in the area. I went inside and talked to the manager about if he would like for me to have work performed today after the storm has passed he said have a tech return tomorrow morning to take care of call. I got my signature and left store. Updated dispatch. Follow up needed | Nuisance Calls | Nuisance Calls | 0.99838
Travel 0800-1100 Onsite 1100-2030 RTU 21-arrived onsite checked in with MOD Todd received roof access located RTU r/r compressor liquid line drier and contactor checked weld with nitro then pulled vacuum pull 500 microns added 11.13oz of 410a started unit up then we found TXV not working properly had to recover refrigerant and removed and weld in a New TXV pressurize with Nitrogen check welds then we pull vacuum to 500 microns added the refrigerant that we had recovered RTU 21 back online delta T 20° split SC to compressor 20° coil temp 40° monitor server room temp and it’s at 72° offices down stairs are at 76° and still dropping Informed MOD of job performed and checked out | Compressors/Motors | Compressors/Motors | 0.99862
8/11 Jeremy McCool entered into Service Channel: Troubleshot unit and found bad point on output module 32 at Rack. Changed point to output module 33 and got with Novar, checked system all cases working normally at temp and defrost working properly. Communication is down for output module 32 and is being ordered. 8/10 Cory Authement entered into Service Channel: Checked cases ran cases through defrost checked with manger will product rmeoved in the morning to de ice coils found is staying in defrost found to be bad defrost Board 32 Boards needs to replaced 8/9 Cory Authement entered into Service Channel: Checked cases ran cases through defrost checked with manager will product removed in the morning to de ice coils | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99727
Anthony Robak Checked in with MOD Jordan Went to case B5D and found it at temp Found who put the ticket in and they meant to put in MTB-11a and b Went to case MTB11 a and b and found it at temp Checked airflow and all cases had good airflow Went to rack B to check temps and found all four coils reaching setpoint of 31 degrees Went to case and used temp probe and showed management temps of each case All cases on B11A and b at temp Explained to management that product has to be behind airflow line or else product will not be at temp Went up to RTU 6 to check ops because of case humidity Found compressor 2 off on hhp Found bad fan capacitor and replaced with capacitor CR10X440 All condenser fans up and running Reset comp 2 and checked pressures First stage cooling now back online Checked AHU 1 ops which serves area that the case is in AHU is running properly The excess humidity in the case is due to general high humidity in the area Case is also next to meat and chicken prep area While on site, found compressor B5 off on oil safety Checked contactor and it checks out Oil safety working properly Reset compressor and checked oil pressure Oil pressure is same as crankcase pressure Compressor B5 needs oil pump replacement Will order oil pump for comp B5 Valved off compressor and left toggled off with note Checked out with Chelsea parts on order | Compressors/Motors | Compressors/Motors | 0.99854
Complete. Checked in with management upon arrival. Checked bs04a and was still leaking. Resealed and caulked inside of case and left to dry. Checked Bs05a and a10a and located leak. Asked to have product moved and cleared racks and covers. Found clogged screen around drain. Removed screen and standing water drained. Cleaned and rinsed screen and blew out drain with compressed air. Poured water and drain was clear. Saw no leak. Returned to bs04a and poured water and notice case was still leaking. Removed metal bumper guard and from trim piece. Noticed water was leaking all across back of case behind evaporator. Panels are old separating due to age of case. Recommend to manager case should be replaced. | Capital Replacement | Capital Replacement | 0.98259
Time in 2100 Time out 2115 Checked in with manager Benny. Hussmann M# RGD-30D-72H-4-S/C S# 1030514201836193 The case is a self contained case and compressor was not running. Checked wiring and found loose wire that came off start relay. Put wire back on and compressor turned on. Case temperature dropped. Cleaned Honeycomb and condenser coil and case is now cycling off and off properly. Checked out with manager Benny. Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99681
1630-1700 travel 1700-1815 Travel OT 1815-2030 OT Called out for cafe cooler warm Met with manager Inspected and found unit not pulling down to suction pressure. Gauged up to unit on rooftop and found unit cycling off on thermal overload, compressor pulling down to 85psi and then building pressure back up to 95psi (suction), head pressure sitting at 300psi. Not going off on high head pressure, compressor has failed will not reach suction. Quote to RR compressor | Compressors/Motors | Compressors/Motors | 0.99863
8/8/2023 3:02:08 PM Brooks, Byron -0001 Time in: 1515 Time out: 1645 located case BS-2 Temp reading 38 Product blocking means of service Removed product Found product had bent back pant onto coil reducing airflow Shut off refrigerant valve Case has good airflow Both fans are working properly Used water to de-ice coil Plugged fans back in Turned refrigerant valve back on Reassembled case Checked out with MOD call complete | Damage by Customer | Damage by Customer | 0.98053
7/18/2023 1:54:09 PM Alcaraz, Jose -0001 Time in 1500 Time out 1600 Call completed Log into service channel and check in with manager for bs03 high temp -found motor unplug and light unplugged -plugged fan and lights -fan back online case running at set point -ran case thru defrost -case running at set point | Nuisance Calls | Nuisance Calls | 0.99844
Time in 1830 Time out 1845 Checked in with manager Oscar. MTBS14a M# OM8NRG S# 1099146 Tg# 0035447 BS05a M# OM12NRG S# 1098626 Tg# 0035472 This was a duplicate ticket , took care of issue on first ticket for this. Checked temperatures of each case. All are not in alarm. Complete | Nuisance Calls | Nuisance Calls | 0.99837
cs3-4 were blowing out water after defrost. I called novar to look at the defrost. there was no drip time or fan delay in the parameters. they set it to 5 mins for both. I will return next week to follow up | Nuisance Calls | Nuisance Calls | 0.99828
Travel: 0830 Time in: 1000 Time out: 1600 arrived at sams club Checked in with MOD assisted lead tech with changing oil controllers for compressor 3 on rack BS and number for on rack B Went inside sams clubs and located bunker A-7 Both boards on sides were off Went to Home Depot and got utilities to fix side panels Fixed side panels Checked out with MOD Call complete | Compressors/Motors | Compressors/Motors | 0.99859
8/19/2023 10:48:50 PM Maldonado, Chris -0001 Start time-2200 End time-2230 complete checked in with manager Raymond hayden arrive to dairy cooler MITB-5 ° MTB-6° at set point 31 degrees called home office to confirm (MITB-5 ° MTB-6° running at set point) checked out manager Raymond hayden | Nuisance Calls | Nuisance Calls | 0.9982
8-2-23 Paul Z / MTA 4 drain pan is iced at drain checked in with Andy found WIC MTA has two iced drain pans sizer lift is not working will have to speak with Jeremy in the morning about possibly renting a sizer lift. cooler is at temperature with no alarms Incomplete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.998
8/18/2023 2:37:49 PM Enciso, Juan -0001 Checked in with colt . went ahead and checked out the case and the case had a fan turned off because someone tried to put the plastic covers and the fan broke one of them and got stuck, fan wasnt running. case was also iced up. I turned off the valve and grabbed the blue water cart. Began to taking off the panels, after when I took them off I began spraying hot water, melted all the ice and cleaned up the case, took the blue cart to its place while the case dries up a little, after when I came back I put everything together and opened the valve on . Waited for the case to come down on temp. Temp is now at 34 degrees. Talked to Chris about the situation and checked out. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99833
8/9/2023 3:34:11 PM Maldonado, Chris -0001 Start time-1630 End time-1730 complete checked in with manager Sabine at temp upon arrival moved product to case MTB-11a took case apart to see if iced up (not iced up) called home office to see if call came in because of defrost temp 26 set point 25. defrost-Termination at 4 per day 25 min 45 degrees Changed set point from 25 to 28 and changed defrost 25 min to 35 min Checked out with manager Sabine | Nuisance Calls | Nuisance Calls | 0.99833
SYS:Rack C Brand:HILLPHOENIX Mod:PS SN:121115 Compressor two dropped by oil was identified, it was reset and left working. I checked voltage and everything is fine. Manager Leo | Compressors/Motors | Compressors/Motors | 0.99858
TT 0730-0900 St 0900-1100 Call completed Arrived log into service channel and check in with manager for produce WIC high temp -check controller found circuits going into defrost and the same time -called Novar had them change defrost to schedule defrost with a 10 min delay before the next circuit goes into defrost -waited for cases to drop temp | Nuisance Calls | Nuisance Calls | 0.99837
8/8/2023 2:53:38 AM Cosgrove, Reese -0001 On-site 1015-1230 Arrived on site. Checked in with manager, Jacob. Model: TD600-081-VC-4-FHSLX-B Serial: 1201000039 R407a refrigerant Made way to motor room to check rackB. Receiver level is at 30-35 Suction pressure @ 41psi Discharge pressure @ 280psi Transducers are reading correct pressures Monitored rack as compressors cycled to check receiver level All cases are reaching desired set points Receiver level dropped to 20% while monitoring Will return tomorrow to add refrigerant and perform leak search on rackB job incomplete 10/19/2023 12:06:39 PM Hooper, Zackery -0002 10/19 Checked in with manager. Performed follow up leak search on rack B. Checked motor room, condenser and sales floor for any potential leaks. Receiver level is currently at 50%. There were no leaks found on any areas for rack B. Will not haft to add any refrigerant to the rack. While checking for leaks in the motor room I found that compressor 4 on rack B was in a motor protection trip on the coresense protector for the compressor. I was able to trouble shoot and find that the winding’s resistance are reading high at 0.85 ohms and the Compressor windings are only rated for 0.35 ohms +/-7% per the manufacturer. Ohm readings on the windings are well out of the 7% threshold given by the manufacturer. Tagged out the compressor and will need put in a quote to replace it due to high winding resistance. Attached is the data tag for the rack, data tag of compressor, coresense module, and Adjustable oil regulator that will need to be ordered and replaced, including 1 3pole/50amp/208-240v contactor. 2 techs / 10 hours each Also attached is a screenshot of the line to line rated winding resistance and the current winding resistance reading. Verified all electrical connections were tight and secure. | Compressors/Motors | Compressors/Motors | 0.99856
Jul 25, 2023 Found WIF at 0° at arrival and both cafe boxes with doors not latched. Ice buildup is from doors not being closed, shut doors. Employee reopened doors and did not close it behind them. Looks like a combination of doors open after a defrost. No other issues found unit at 1° but started a defrost 5 minutes ago. | Nuisance Calls | Nuisance Calls | 0.99792
8/17/2023 10:03:08 AM Arriaga, Luis -0001 Arrived on site checked in went to motor room and found compressor running checked date on when it came in call had came in when rack went down compressor is running checked out | Compressors/Motors | Compressors/Motors | 0.99859
Make: hill Phoenix Model: O5DM8 Serial: 1309422 Unit: 4.2 -upon arrival case was at 61f with no air flow and all the products were pulled. -disassembled case and found drain plugged and one fan motor was out. I cleared drain line then washed drain pan and flushed drain line. Evaporator fan was replaced also. -reassembled unit and started it back up. Wait for case to pull down to temp. Case pulls down to temp. No other issues system operational. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99821
replaced all 6 condenser fan blades on rack b condenser. air flow has improved and discharge pressure is running 240-250. | Compressors/Motors | Compressors/Motors | 0.99779
7/17/2023 11:33:48 PM Stuart, Christopher -0001 Time In: 2215 Time Out: 0045 Checked into Service Channel Checked in w/MOD Kurt Rack DTB Low Suction Alarm (Home Office Alarm) The entire club lost power, and caused all three racks to go offline. Rack DTB low suction alarm tripped as a result of power loss. All racks are back online. DTB alarms are cleared. Pressures @ 37/236 Checked out w/MOD Kurt Checked out of Service Channel Job Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99721
EnRoute: 13:25 Time In: 13:50 Time Out: 16:50 LTA-01 -1 LTA-02 1 LTA-03 2 LTA-04 defrost Arrived and checked in with manager, made my way back to the freezer and found A04 running warmer than the rest of the others. Verified all fans were running and no ice build up on coils, went to rack and checked receiver level and if sight glass was flashing. Sight glass was solid and receiver level was fine. Did find compressor 3 was off on temperature control, I reset the switch and comp 3 started running. Went to check condenser 1 motor not running. Will pick up motor from parts house and return on follow up to replace, part should be local. Temperatures for A01-3 started dropping they are running at -1 to 2 degrees while A04 is in defrost. Ran everything I found through team lead. Checked out with Raymond Jerek | Compressors/Motors | Compressors/Motors | 0.99852
Job completed I was at the location for another call. Spoke with the MIC Ryan milliff about the door gaskets on the ice cream cases. Unboxed six door gaskets from packaging. Use my pliers to remove six door gaskets on cases a6a and a6b the ice cream cases on the back wall. I use a food grade lube to reinstall the six reach in door gaskets I adjusted two doors so they would close properly. Everything is working correctly at this time. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99737
7/17/23 TH Time in: 20:45 Time out: 21:00 Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643 Arrived on site and checked in with Service channel and MOD(Justin). This called is duplicated the PO#251141303. Informed and checked out with MOD(Justin) and Service channel Job finished | Nuisance Calls | Nuisance Calls | 0.99844
TT 1730-1815 Time in 1845 Time out 1930 Call complete Arrived log into service channel and check in with manager for rack A high super heat -found controller in comm loss -reset controller -cases all went down to temp -receiver level at 30% -all fan running on condenser | Nuisance Calls | Nuisance Calls | 0.99821
8/1/2023 4:09:23 PM Authement, Corey -0001 Checked cases on cases A9.1 2 and 3 was running in low temp trouble shooting problems find to be the setting on controller was wrong Novar re down setting now cases are working correctly | Nuisance Calls | Nuisance Calls | 0.99821
On-site 0930-1245 Arrived on site. Checked in with manager, Brad. Found ice cream freezer high temping Removed product to inspect evap coil Found evap coils frozen Deiced evap coils until all ice was thawed. Cycled system through defrost Defrost cycle was not working for a03b Found wire for heater burnt and disconnected Cleaned up wire, reconnected with wire nut. Cycled through defrost and confirmed operations Monitored freezers to ensure temps dropped within range Freezers we’re all below 0° before tech left Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99865
Checked in with manager Cheryl, this is not a recall, the manager marked this call unsatisfactory because there was confusion about how this was to be resolved. They wanted to lower the temp set-point in the room and needed to have corporate change the set-point. I was able to change the set-point last time but only by a few degrees. So they need to contact corporate to make bigger changes to the set-point. I called building support and had them confirm the RTU is at a set-point of 71F and it is currently at 71F. I had them annotate it in the work order as well. LENNOX RTU 23 MODEL # LGE060H4BH20 SERIAL # 5604E03211 I spoke to the manager and let them know that the RTU is working properly and that they need to have corporate make the change to the set-point if they want it colder but right now it is set to 71F and is currently at 71F. Checked out with manager Cheryl Call Complete | Nuisance Calls | Nuisance Calls | 0.99828
Start time-1730 End time-1900 checked in with manager Demora lyons checked case MT-SC3 MD PIZZA MT-SC5, case at temp called home office to confirm temp they said no alarms and it’s reading temp checked out with manager Demora lyons | Nuisance Calls | Nuisance Calls | 0.99835
8/8/2023 8:54:36 PM Stuart, Christopher -0001 En Route: 1845 Time In: 1945 Time Out: 2200 Rack B Multi-Compressor Lockout (Home Office Call) Issues: Gained access to Rack B and the condenser was running on arrival. All compressors offline, in HDP L/O Comp 4 L/O would not reset. Pressures @ 70/260 on arrival Work Done: Reset all compressors. All came online except Comp B4. Called Novar and they could not access the rack, because it was in comm loss. Unplugged the ES1 for 15 minutes and plugged it back in. Alarms finally cleared and Comp B4 came back online. Suction pressure dropped down to 32 psi, set point @ 35. Monitored rack for awhile to ensure no further issues. All cases at temp. Job Complete | Compressors/Motors | Compressors/Motors | 0.99854
7/19/2023 4:01:03 PM Balstad, Michael -0001 Roll Seal Model #: SC-325 Serial #: 0005222 Call for roll door for W/I A1/A2 getting stuck/not closing. Arrived and checked in with manager. Located W/I and inspected. Roll Seal controller giving “EOF1” error code. Error code for Encoder Signal Lost. Contacted Shane with Roll Seal for tech support. Flipped motor safety bar back into proper position. Found emergency cord had been pulled out too far. Re-inserted emergency cord back into position. Reset controller. Opened door fully to set parameters. Closed door fully. Door now opening and closing properly. Cleaned work area. Checked out with manager. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99682
8/2/2023 12:22:58 PM BOWERBANK, MATTHEW -0001 cs3-4 were blowing out water after defrost. I called novar to look at the defrost. there was no drip time or fan delay in the parameters. they set it to 5 mins for both. I will return next week to follow up 8/7/2023 9:20:25 AM BOWERBANK, MATTHEW -0002 last week on first visit water was dripping from the case during defrost there was a slight bit of ice build up on the inside track but not in the pan I removed the ice and have them change the defrost settings came back today everything looks fine spent time on phone with tech support going over defrost parameters the case is now set to go through 6 defrosts per evaporator per day | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99824
7/24/2023 11:33:58 AM Vargas, Fernando -0001 Time in 1015 Time out 1130 Had to reschedule with MOD Kris Evaporator coil leaking water MOD wants us to return at night when store is closed Informed Supervisor Sam regarding reschedule Rescheduled for 07/24/24 20:00 Follow up 7/26/2023 2:09:13 AM Vargas, Fernando -0002 Travel 1730 Time in 1900 Time out 0200 Water leaking from coils and fire sprinkler in dairy cooler Arrived on site Checked in with MOD Reported that light was out in dairy cooler Couldn’t open cooler until 2015 once all customers were out the store to work in Had to work with no light whole time Accessed scissor lift Reported that a few coils were dripping water on floor Fire Sprinkler as well leaking Informed MOD that we can’t work on the fire sprinkler Coil MTC-6 dripping water had a sweaty drain pan as well Took off both drain pans Inside evaporator coil, fans, and drain pan were dirty Cleaned evaporator coil, fans, and drain pans on coil MTC-6 and MTC-4 Reassembled coils Quoted out MTC-1, MTC-2, MTC-3, and MTC-5 to be cleaned 2 techs 16 hours night job OT Approved by Supervisor Sam Lopez Checked out with MOD Mike FU Needed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
Travel 0700 Time in 0830 Time out 1015 Case B10 fan out Arrived on site Checked in with MOD No airflow from right side of B10 case Had employee pull product Fan was out Fan outlet pulling 115v Fan had been wire nutted Checked fan plug Fan plug pulling 115 V Fan plug wire but became loose Rewired fan to fan plug Fan energized and working fine Put fan back on plenum Put panels back on Checked out with MOD Kris Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99675
Checked in with manager Ellen, checked the unit and the board was frozen, I reset the unit by power cycling the RTU and the unit started up on its own. I called Novar to confirm temps and they said it was set to 73F and currently the unit was at 73F. History showed someone had changed it to 68F some months ago and then it was changed back by corporate. I checked pressures to ensure it wasn’t low on refrigerant. I checked the fan operation and it is running, I checked blower and it was running normally. I checked temp sensors and they are running normally. Unit is running properly and there is no alarm present for this unit. I let the optical associate know that if they want it changed permanently they need to have their manager submit a change request form to set it. Other than that, the unit is running and operating properly and at target setpoint. Confirmation by Novar. LENNOX RTU 23 MODEL # LGE060H4BH20 SERIAL # 5604E03211 Let the managers know the unit was running properly. Checked out with manager Antonio Call Complete | Nuisance Calls | Nuisance Calls | 0.99812
At site meat case leaking water. Removed rail in front of case then kick plates. Located drain that’s overflowing due to floor drain being clogged. Cleared floor drain case started draining poured hot water in case for about ten minutes draining properly. Placed kick plate and rail back in place. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99838
7/28/23 TH Time in: 17:00 Time out: 18:00 LTA-4: DT CFN HUSSMANN MN: F-8G SN: MY18H064792 Arrived on site and checked in with Service channel and MOD (Hilda). Checked the case is good airflow. Checked the temperature sensor showed -12 degrees F and no alarm present. Checked graph temp is good. Found the system was loss Communication. Fixed it. It’s on line and No found issues and no alarm present. Informed and checked out with MOD (Anderson) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99841
8/22/2023 5:49:38 PM Bonner, John -0001 Rack B Kysor warren Model -TC430-056-DC-4-NVG-B Serial -0203000236 Checked in with manager on arrival. Call placed for high suction pressure on rack B. Gained access to rack and checked OPS at co troller. Found BS group running @ 49 # suction . Spoke with home office and found no active alarms on rack B. Ensured compressors are online nothing tripped. Checked suction valves at compressors and ensured no valves blowing by. Gauged up to rack and ensured transcode pressure. | Compressors/Motors | Compressors/Motors | 0.99853
Arrived on location checked in with the manager she information me that JO was out two days ago for rack A comp 5 lock out I gained access to the rack house and found comp A1 locked out on oil with oil in the reservoir I reset the oil safety and watched the compressor run it showed no signs of oil issues during operation sitting with in recommend oil levels per manufacturer specs I performed a pump down test on the compressor and found no issues I did find flood back to comp A5 which receded once a system went into defrost so I cleaned up and locked up the rack house I did a quick scan over all the refrigeration equipment to verify there was no other issues I informed the manager and I gave here the tracking number for this call so she is aware what I looked over and checked out call complete | Compressors/Motors | Compressors/Motors | 0.99856
Sams 4718 South Jordan 7-17-23 Wo 230716-0187 Po 251002158 MTB compressor 5 L/O Follow up to return and replace oil fail module Compressor B5 Travel 0945-1000 On job 1000-1300 Found compressor off Reset OPC Compressor came back on Checked net oil 40psi Found high discharge pressure 285 Found 2 CFM not spinning Checked windings both motors ok Checked shorts to ground non Found Found both motor overloads open Reset overloads Motors came back on Compressors and all CFM now operating Let compressor run while working on other compressor Checked back on compressor Compressor tripped again Could not reset Compressor Checked sentronic oil fail When oil control open it has 208 v When oil is closed looses 120v Need to return And replace oil fail control | Compressors/Motors | Compressors/Motors | 0.99855
En Route: 1730 Time In: 1815 Time Out: 2015 CPU Freezer Running Warm Checked into Service Channel Checked in w/MOD Katrina Kysor Warren (CPU Freezer) M# FX5SL-03RUN S# C17H00393 R-404a Located CPU freezer. Case controller displaying an ER 7 alarm and case temp at 59. Removed deck pans and the fans were not running. Slight ice build up on distribution, suction line and in the middle of the coil. Put unit into manual defrost and de-iced coil with hot water. Put case back together and terminated defrost. Case temp got down to -2 after about an hour. Set point is -6. CPU freezer is right next to two exit doors, and constant opening and closing the doors let’s large amount of warm air into the case and ices up the coil. Checked out w/MOD Katrina Checked out of Service Channel Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
Completed Arrived met with manager.was shown deli case BS04A drain was clogged with old food. Cleared drain and washed out pan. Tested and drain is working properly. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99844
7/20/2023 11:45:27 AM Hanamornsate, Thirathanawat -0001 7/20/23 TH TT: 8:00-9:00 Time in: 9:00 Time out:13:30 Air Curtain: Receiving Room Berner Product no: EJ866 Checked in with Service channel and MOD(Justin). Checked the location. Found the breaker on the unit was turned off. Turned it back on and found bad Door sensor and unit hunting for turn on and turn off. Talked with MOD (Justin). He needed to put the manual switch for turn on and off for this unit and needed to be cancel the Door sensor. Went to the Home Depot for pickup parts and went back to the store. Installed manual switch and ran the conduit and Electrical wire for this unit. Checked operation it with MOD (Justin). It’s working good. Cleaned work area. Informed and checked out with MOD (Justin) and Service channel. Job Finished | Nuisance Calls | Nuisance Calls | 0.99822
7/14/2023 10:42:27 PM Alatorre, Mario -0001 07/14/23 Mario. A Sam4824 W 230714-0222 F/U Follow up to replace 4 Condenser Fan Motor. Info US Motors Model#J63wzGSG-0263, CAT#SWA010905-SGR. , HP 1/2, RPM575, volt 480, amps 1.0, Frame 56HZ. Call Hi Suction and Discharge Rack. Discharge @ 321psi / suction @ 52psi, -Check Air Cool 4 of 12 CFM out, open reset bottom on mag start contactor in control, fuses check out. -RLA on CFM 1.0 amp, pulling 6.0 amp and shutting down opening mag start contactor. Setup sprinkler front of condenser to help, discharge@ 269psi turn ON water sprinkler discharge drop @ 235psi, but need to replace CFM. 7/17/2023 11:30:29 AM Alatorre, Mario -0002 07/17/23 Mario. A Sam 4824 W 230714-0222 F/U Arrived at parts house for CFM in stock, needed fan blade for CFM motor, drove an arrived onsite removed fan blade drove back to parts house, motors will be available follow day, f/u to return next day for repairs F/U 7/18/2023 6:27:39 PM Tobar, Ricardo -0004 At arrival checked into SC app and with Michelle. Assisted with R/R 4 CFM on rack B. See Mario A. Notes for further details. Call complete. 7/18/2023 6:28:44 PM Alatorre, Mario -0003 07/18/23 Mario A Sams 4824 W 230714-0222 Arrived onsite check in with a manger on duty for repairs on Air Cool Tower -Removed and installed 4 new replacement CFM -Check amps drawing @ 2amps -Discharge @ 307psi / with replacement motors discharge @ 263psi -VSD back to auto Complete | Compressors/Motors | Compressors/Motors | 0.99822
7/19/2023 4:51:05 PM Fenton, Typhan -0001 Make: Heatcraft Model: LET047BK Serial: D03A06987 Unit: MT1 -upon arrival case was at 40f with evap coil iced up and drain froze over -checked system and forced defrost and defrost works. I then decided coil and system was diagnosed with a bad defrost timer. -I picked up defrost timer from United then returned and installed and rewired to match newer model defrost. Timer was set for 30 minutes 4 times a day as previous timer. -reassembled system and turned system back on. Case pulled down to temp. No other issues system operational. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99861
8/5/2023 10:58:08 AM Johnston, Andrew -0001 Checked in with Heidi then began checking the cases. Found both S3C controllers were in comm loss. Cycled power to each unit then verified the sensors and transducers were reading correctly. The systems are running well but were alarming for high temp at the end of the defrosts due to the comm issues. Both systems are running well and are near setpoint. Checked out with Heidi, call complete. 8/31/2023 2:31:38 PM Calderon, Jose -0002 Checked in with Heidi, this is not unsatisfactory, the manager did not know why they marked it unsatisfactory since it is running at temp. Temp set-point is 29F and current temp is 30F. Set point for superheat is 6F and current superheat is 6F. Checked history and it shows no signs of high temping since the last time tech was on site. Unit is not in comm loss. Called Novar and confirmed there are no issues currently. MTC09f CASE HUSSMANN MODEL # IC2SM8 SERIAL # MY21G068835 Current temp 30F Let the manager know that the case is working properly and has no history of high temping. Verified with Novar that there are no alarms for this case. Checked out with manager Heidi Call Complete | Nuisance Calls | Nuisance Calls | 0.99835
Heat-craft M#BEM0475MS6EMAY09 S#T20J24461 I had arrived to store and check in with the manager then diagnosed the wall freezer A4a it frost around the evaporator then I turn on the compressor.then got lift to wash the coil and remove the ice build and curtains was bend so let hot in then I adjusted the curtains and the cement floor has a holes where hot air goes in the wall freezer and put on defrost the heater are working this work order is complete.7/21/23 | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99847
7/22/2023 10:33:54 AM Jones, David -0001 Located self contained cooler and found compressor short cycling also noticed hard-start capacitor got disconnected on one side. So I rewired capacitor and got compressor. Temperature dropped and cleared alarm | Compressors/Motors | Compressors/Motors | 0.99858
Time in: 13:45 Time Out: 16:45 Assisted lead tech lit clean coil and unclog drain lines and clean cafe walk in cooler. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
Arrived at the store logged into Service Channel and spoke with the manager Robert. I looked at rack A and found all compressors working properly photos attached. I spoke to Robert and told him what I found and what I did. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99817
On-site 1230-1315 Arrived on site. Checked in with manager, Jacob Made way to rackB. Checked comp5 on rackB Compressor was not in lockout on arrival Monitored compressor temporarily Checked gas and oil pressure on compressor All checks okay call is from July 17, possible duplicate Job complete | Compressors/Motors | Compressors/Motors | 0.99864
7/21/2023 7:02:25 PM Schrock, Kevin -0001 Measured air curtain and will have replacement ordered | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99532
7/17/23 Ray Gary Arrived onsite and checked in with the manager (Mario)Located the case and the issue was the drain screen was plugged So I cleaned the screen and blew the drain out with nitrogen Ran warm water to ensure proper draining No other issues were found HUSSMAN M#-ID5SM8 S#-MY18G060369 THIS CALL IS COMPLETED | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9976
7/28/2023 4:22:55 PM Alcaraz, Jose -0001 Time in 1600 Time out 1830 Call completed Check in with manager for C03b high temp -found case ice -check set point at 13 -de-ice case -called home office had set point changed to 23 | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99808
Assisted Jake with compressor replacement. | Compressors/Motors | Compressors/Motors | 0.99853
7/27/2023 3:27:08 PM Camacho, Raul -0001 TT 1100 check in 1230 checkout 1530 Check with manager at the arrival and check RIIC case sys A5b found case with not air flow, evaporator coil was iced up I asked manager to remove product to deiced evaporator coil, deiced evaporator and check heaters , defrost system is working properly, no more problems found | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
7/27/2023 5:07:02 PM Stuart, Christopher -0001 En Route: 1600 Time In: 1715 Time Out: 1815 C18a DT DELI High Discharge Air (Home Office Call) Checked into Service Channel Checked in w/MOD Jimmy Call is a duplicate. Located case, and it was at temp. Call was resolved 7/25. Fans were up plugged during a case cleaning. No further issues Checked out w/MOD Jimmy Checked out of Service Channel Job Complete 7/27/2023 5:08:20 PM Smith, Stephen -0002 EnRoute: 16:00 Time In: 17:15 Time out: 18:15 Assisted lead tech | Nuisance Calls | Nuisance Calls | 0.99826
Time in 1600 Time out 1630 Checked in with manager Ron. B10 M# ADT130AK S# D05L16490 Fan is not making any noises at all. Turned motors off and back on, there were no abnormal noises at all. Manager Ron said to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.99835
Favian Porrata 07-26-23 Travel 0730 Arrival 0845 Departure 1200 Upon arrival checked in with Manager Peter. Call was for follow up and install new float in swamp cooler. Had to wait to get roof access. Once got access to roof started off by powering down unit. Turn water line off. Took apart old float. Installed new float in to system. Made sure to level float correctly. Turn water back on to check for any leaks. No water leaks. Turned unit back on. Call complete. | Capital Replacement | Capital Replacement | 0.988
8/8/2023 1:14:44 PM Armstrong, Ludwig -0001 SAMS CLUB 4843 Travel 20:00 21:00 Labor 21:00 22:15 RTU15 Make Lennox ModelSCC06OH4B03037 Serial 5612B03037 Unit as leaking water into the cafe. Discovered unit evaporator coil iced up. Disassembled compressor. Will return in the am to diagnose unit. 8/8/23 Travel 10:45 11:00 Labor 11:00 15:00 Discovered unit low on charged. Added 5lbs of R410 refrigerant system holds 18lbs. Visually inspected unit for refrigerant leaks no sign of leaks. Checked evaporator drain. Found debris in drain. Cleaned drain will close call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
Gp230729-0082 1230-1530 ot Checked in with manger worked on BS6B island Wo252146338 Found coil iced up deiced coil and pumped down system cleaned screen also cleaned drain and made sure everything is working correctly case back to temperature showed manger | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99867
Arrived on-site checked in with management checked rack MTC compressors 1 and 2 found both compressors operation noticed compressor 3 had pitted contactor went ahead and shut compressor 3 off installed new co factor checked operation all compressors are working properly at this time. | Compressors/Motors | Compressors/Motors | 0.99856
Job complete Arrived onsite and checked in with management. Located cooler and found one fan out. Used lift onsite to access fans and found power wire shorted out and not making contact to motor. Once I fixed wire motor still did not come on. Took motor out and put case back together. Went to two different supply houses due to first one didn’t have it in stock. Once I had part returned to store and used lift to replace motor. Once replaced, turned power back on and monitored for normal operation. Motor is working properly, explained to management and checked out. | Compressors/Motors | Compressors/Motors | 0.99824
8/1/2023 4:08:25 PM Authement, Corey -0001 Checked case remove coves cleaned out pan cleaned out hose to pan put back in service | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99823
8/17/2023 2:59:46 AM Authement, Corey -0001 Have added water hoses and sprinkler to condenser to keep head pressure in range due high temperatures and coils are deteriorating all compress running | Compressors/Motors | Compressors/Motors | 0.99858
7/26/2023 10:06:13 AM Angelle, Troy -0001 Found compressor shorted to ground. Have new compressor on order. Will return to install once in. 7/31/2023 4:49:06 AM Angelle, Troy -0002 Replaced shorted compressor. Pulled vacuum, and recharged to factory specifications. Let run to set point of 29°. | Compressors/Motors | Compressors/Motors | 0.99859
7/16/2023 1:21:03 PM Cervantes, Carlos -0001 Travel: 0630-0830 On-site: 0830-2030 On arrival checked in with store manager. Stated that all cases for rack B are running warm. Went to compressor room and found no compressors running. I immediately got odor of burnt wiring. After investigating found that contactors for comp#1 and #2 were completely fried along with auxiliaries. Checked both compressors for any possible shorts and and found compressor#3 had open windings and compressor needs to be replace. Compressor was still operational condition. Replaced contactor for comp#2. After continuing to troubleshoot found that control voltage breaker was tripped and rested. Once resetting i started up rack except comp#3. Monitored and rack struggled to come down to suction. Saw that compressor 5 for rack was toggled off and check to see if its in operational condition. Compressor was in operational conditions and started up comp. Rack now is holding proper suction. As i am monitoring i noticed that controller had a active low level receiver alarm. Did verify i had no liquid level percentage on indicator and had a flashing sight glass. Leaked checked rack and found no leaks. I then leaked checked store and immediately got hits on my leak detector as soon as i went inside; indicating a big leak. After spending time leak checking I finally located leak at the cat walk of walk in cooler on sys B4. Leak was at the suction pipe. Made repair and leaked checked. No more other leaks found. Picked up 480 lbs of 404a. Rack only took 288lbs of 404a. Will return extra refrigerant. Rack is now at 30% receiver level. notified manager about all findings and CALL IS COMPLETE. | Compressors/Motors | Compressors/Motors | 0.99855
07/25/2023-Glenn Sr. and Bob E. Tech on site. Proceeded to merchandiser freezer. Found condensate pan overflowing cause water to leak onto the floor. Found condensate pan burned out drove to parts house and picked up new condensate pan. Installed new condensate pan and cleaned evap coils with brush and coil cleaner. Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99816
DESCRIPTION: INCOMPLETE! Found the AC unit, RTU-7, IAQ on the roof. The compressor #3, and #4, working fine. The compressor #2 was not working. Required for compressor #2, then it works. There was a small leak from the high side service port. Tightened the Schrader valve core. Will change gas to compressor #2 tomorrow. | Compressors/Motors | Compressors/Motors | 0.99857
took freezer door off POS freezer. installed new heaters and gaskets installed door. we are missing a leg of power also and will need to come back and further diagnose. door is now back onto freezer. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99734
7/15/2023 10:20:33 AM SMITH, ANTHONY -0001 07:45 am -1100am (3.25 AFH) Arrived on site with primary tech James. Checked in with MOD. Walked into bakery and inspected freezer door. The door isnt sealed correctly because it looks like it was hit with forklift. We tried to adjust the door, but the weight of it wont let it sit right. Will have to return with brackets and cement drill to fix issue. | Damage by Customer | Damage by Customer | 0.98644
7/22/23 SH Tt 09:00 St 10:00 Et 13:00 B7 Meat case M-NMG-12 S-4532973 Upon arrival checked in with mod and ivr Located cases on sales floor Found product already pulled Removed deck pans and found case with no frost pattern on valves Gained access to machine room Found LLSV for B7 not pulling any amps Stemmed in solenoid stem for now, to get case to drop while troubleshooting Removed cover and checked voltage at wire nuts No voltage, loosing a leg of power Checked controller and located board and point for circuit Verified RO point closed Traced wires back and found wire had slipped out of wire nut Placed new wire nut Verified solenoid now energized and pulling 10Amps Waited for cases to pull down in temp At departure both 7A/B at 30F and 28F Call complete | Compressors/Motors | Compressors/Motors | 0.99816
8/21/2023 Bob E Tech picked up door and parts and drove to location. Tech check in with service channel and store manager on arrival. Removed damaged door and installed new Anthony door. Adjusted door swing. Tested door multiple times. Door now working properly and sealing properly. Tested anti sweat heater and is working properly. Job complete Also took broken door for disposal. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9971
8/1/2023 5:46:56 PM Hanamornsate, Thirathanawat -0001 8/1/23 TH TT: 8:00-8:45 Time in: 8:45 Time out: 11:00 LTA-2: Rollseal Door MN: RS-500 Track Kit SN: 0009113 Checked in with Service channel and MOD (James). Checked the location and found Rollseal doors cannot moved because the blanket was tangled. Turned off the power. Unlocked the breake of Motor and managed the Rollers and Blanket. Locked the Breake of lift motor. Turned on the power and set programmed to the Manual mode. Checked Door operation. It’s can open and close now. This Door needed to be replace and New Door is already order. Just waiting shipping to the store and replace in another work order (Refer WO# 230625-0059). Cleaned work area. Informed and checked out with MOD (Josh) and Service channel Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99699
0830-1400 labor OT Arrived on site and checked in with manager Jeffrey Located system MTB5 meat walk in cooler Both evaporators in walk in leaking water from drain pan Used scissor lift to reach evaporator coil Found drain pan clogged Removed water from drain pan Unclogged using nitrogen Deiced the ice build up on the coil and distributor Did the same to other evaporator Evaporators not leaking anymore Checked out with manager Jeffrey | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99866
8/28/2023 12:16:42 PM Monreal, Jesus -0001 Gp# 230819-0001 Jesús Monreal 08/28/23 1200-1330 Rs Check in with mod Check alarm on compressor rack A follow up on the alarm check compressors for properly operation no more alarms compressor rack working properly all temperatures at set point complete | Compressors/Motors | Compressors/Motors | 0.99861
Time in 1630 time out 1900 Arrived on-site checked in with manager and the pharmacy. Went to roof and found unit operating properly. Called monitoring and they said that all rtus are in comm loss. Then they looked in opus and found some rtus communicating and some are not. Went to roof some rtu and ahus are turned off and some have no power coming from main breaker boxes. Also found the set points for the pharmacy at 73 degrees. Monitoring set the setpoint for ac to 71 and system is running now at 71 degrees. Call complete | Nuisance Calls | Nuisance Calls | 0.99839
9/1/2023 5:08:21 AM Authement, Corey -0001 Check cases found cases sweeting found doors heaters not working repaired connections nowThe working will need to replace 3door. Gasket has be order at Unit houma la 9/5/2023 10:14:15 AM Authement, Corey -0002 Replace 3 door gasket due to cuts on gaskets | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99726
Checked case found solenoid open. System was in defrost took out of defrost and found compressor would not run found and repaired a broken control wire for the contactor. System is now operational and returning to temp | Nuisance Calls | Nuisance Calls | 0.9983
En Route: 1230 Time In: 1345 Time Out: 2045 LTA a01/a02 High Temping Checked into Service Channel Checked in w/MOD Veronica Located LTA A01/A02 freezer. The freezer door was already condemned and pending replacement. The door is intermittently operational, but someone disengaged the motor brake, and the door was stuck open. Re-engaged the motor brake, reset the door open/close parameters and the door is operational. Per case temp sensors, temps ranging between 5-15. Coils are not iced. Rack suction pressure swinging between 15-18 psi. Comps 3-5 were not online. Found compressor toggle switches had been replaced, but they were toggled off. Found fuses for control voltage were blown. Replaced fuses and compressor’s came back online. Suction pressure dropped to 13 psi. POS box temp also started dropping closer to set point. Condenser coil was clean and all fans operational. Checked out w/MOD Javin Checked out of Service Channel Job Complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99683
Time in 1030 Time out 1500 Arrived checked in and out with manager Cris Service for break room running warm Upon arrival found RTU 18 indoor blower running but no compressor or condenser fan running Unit would turn on for approx 10 min or less and would turn off Unit was not satisfied when unit would shut off Checked pressures and superheat while running and pressures are ok Found the freeze control connected to suction line after the evaporator faulty reading and incorrect temp and cause the control voltage circuit to open turning off compressor and condenser Bypassed freeze control and low pressure control is still in service Unit will run perfectly fine with low and head pressure controls with out freeze control Unit is running and is satisfying Monitored for multiple cycles of zone temp satisfaction. Call is complete | Compressors/Motors | Compressors/Motors | 0.99859
7/27/2023 4:28:22 PM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Hilda. Grab N Go MTC12D HussMann M# ID5SM12 S# MY18H070729 -Found water trapped inside the drain pan -Request to removed all product -Drain hole clogged due from slime dirt -Unclogged using C02 tank. Poured water and drain water good -Grab wipes and towels, cleaned drain pan. Washed and cleaned drain hole protector also -No ice build up in evaporator. Case reached temp set point -Reassemble case and locate manager -Talked to MOD Hilda and showed her what I did. -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
7/26/2023 5:11:29 PM Ortega, Uriel -0002 GP#230723-0020 0730-1130 TT 1130-1430 RT Traveled to Roswell, NM Arrived at store and checked in store manger. Checking fuel station ac unit not working. Lennox split system unit Model XC13-018 -230 -01 Serial 5806B03579 Found a dirty filter (15x20x1) and defective condenser fan motor. Drove to parts house and got all needed parts. Replaced filter, condenser fan motor, and high pressure switch. Also run capacitors. Unit properly working. Job complete. Note: no zone sensor, unit running on mechanical thermostat. | Compressors/Motors | Compressors/Motors | 0.99735
8/1/2023 12:02:19 PM Maldonado, Chris -0001 Start time-1145 End time-1400 complete check in with manager Oscar 3 glass door not shutting all the way due to master rod loose and rubber gasket not full on tighten master rod on one glass door and took gaskets off off all 3 and readjusted them checked out with manager | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99724
8/20/23 TH TT: 9:30-10:15 Time in: 10:15 Time out: 12:30 Rack C Heatcraft MN: TD400-033-VC-4-OHD-C SN: S17E00058 Checked in with Service channel and MOD(Javin). Checked the Rack C and Found no power supply to the Rack C. Found Main Breaker of Rack C was tripped from Compressor 1. Checked shortage at Compressor 1 is good and no shortage with ground. Found Bad Contractor and Breaker Comp1 was trip. Removed bad Contractor out and Installed new Contractor and Auxiliary switch in place. Connected all electrical wires. Reset Breaker at the Rack C and Breaker of Comp1. Rack C come back to working. Checked all cases and Produce CLR temperatures. They are good temperature and no alarm high temp present now. Cleaned work area. Informed and checked out with MOD (Leandra) and Service channel. Job Finished | Compressors/Motors | Compressors/Motors | 0.99856
7/21/2023 9:53:42 AM Porrata, Favian -0001 HeatCraft M#DX6XN-08RUN S#C17F00512 Upon arrival checked in with Manager Jeremy. Call was for case for not holding proper temp. Started off by checking airflow and found it to be weak. Began to check evaporator coils and found them to be dirty. Also checked honey combs and baffles. Baffles where clean but honey combs where dirty as well. Talked to manager about pulling hose to clean coils and honeycombs. Got access to water and ran hose on top of cases. Cleaned the evaporator coils and they are now clean. Use water to clean Honeycombs and now also clean. Put cases back together and honeycombs back up. Case is now at temp 34. Checked out with manager Jeremy. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99831
7/24/2023 12:06:30 AM Jackman, Nick -0001 OT 2100-0000 TT/OT 0030-0100 Already on site for another wo While checking in with manager saw bs5 a-f warm Manager thought I was here for this call Called dispatch had call sent to me Closed BV let cases deice While deicing found bs5F coil 1 fan plenum not on correctly Bs5F coil 2 sensor bad RR with 10k sensor Now reading correctly Bs5F coil 1 needs new fan assembly Found Bs5B coil 1 fan unplugged Bs5A coil 2 need new evap fan assembly BS5B coil 2needs new fan assembly I then tested every DA sensor Moved location of multiple sensors All sensors are now reading correctly Tested every coil out let sensor Every sensor is reading correctly Verified eepr is programmed for correct steps Both eev and eepr are programmed to 2500 steps Will verify steps from part # in am Will fu in am with parts Will also need to verify control pressure psi It’s set to 43psi converted is about 9 Will also need to submit program change Rs sheet calls for 4 defrosts a day There are currently 6 defrosts programmed I will fu in am 8/17-BILL INCURRED PER TECH, ALL FANS RUNNING. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99804
8/7/2023 12:27:19 PM SMITH, ANTHONY -0002 Found circuit A05 running warm in defrost, called novar found case defrost settings at every 6 hours for 65min, adjusted defrost to 45min every six hours with a 55 defrost temp termination in place. | Nuisance Calls | Nuisance Calls | 0.99825
I came and checked in with the store manager and checked the BS11A and BS11B system and it was found that the evaporator coil was frozen, so it was defrosted by means of hot water and it remains working under observation since LCD is offline so you have to change the program. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99842
7/31/2023 5:41:24 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke with the manager Justin. I looked at the freezer door and got the door number and attached it to the work order. I will leave this work order open until Sam’s Club can order the door and we can install it. 7/31/2023 5:59:20 PM Brandau, Kenneth -0002 Arrived at the store, logged into Service Channel and spoke with the manager Justin. I accessed the roof and looked at the condenser unit for the grab and go case, and after checking all electrical, I found a fuse is blown on one of the main power legs at the disconnect. I removed the fuse and installed a new one. Turned the unit on and it is working properly now. Case is down set temp. I spoke to Justin and told him what I did and what I found. This is complete no need for follow-up. 7/31/2023 6:00:06 PM Brandau, Kenneth -0001 Delete this work order | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99638
8/11/2023 Villafana, Francisco -0001 Francisco V Checked in and out with Marcus. On arrival found roll seal door stuck Cleaned sensors on the bottom and found the safety strap moved Reset safety strap and reset roll seal door. All ops okay job complete. Walmart app will not allow me to check in called to get checked in and out. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99737
7/24/2023 10:19:10 AM Vargas, Fernando -0001 Case B10 fan out Arrived on site Checked in with MOD No airflow from right side of B10 case Had employee pull product Fan was out Fan outlet pulling 115v Fan had been wire nutted Checked fan plug Fan plug pulling 115 V Fan plug wire but became loose Rewired fan to fan plug Fan energized and working fine Put fan back on plenum Put panels back on Checked out with MOD Kris Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99704
8/3/2023 4:11:33 PM Hooper, Zackery -0001 8/3 Checked in with manager. High temperatures at casing was caused from issues at the rack Found that all the compressors were locked out on oil failure due to low oil levels. Added 1 gallon of oil to rack and made sure oil level was above the first sight glass in the reservoir. Reset controller and got the rack back on. All compressors ended up tripping on high discharge due to dirty condenser. Cleaned condensers and was able to lower discharge pressure and got compressors 2,3,&4 back up and running Compressor 1 is down and is having internal mechanical issues. Got with Jim Mortel and he instructed me to isolate the compressor and he will follow up to further diagnose. All circuits are back down to set-points and pressures and temperatures at the rack are within proper ranges . The repairs were made on work order 230802-0231. Followed up on 8/3 to make sure circuit is reaching set-point temperature. | Compressors/Motors | Compressors/Motors | 0.99852
Start time-0915 End time-1245 complete logged into service channel checked in with manager Vivian took case B06A and B apart to make sure not iced up drain is cleared called sporlan waited for a call back never called me back called Sams teach support to check set point and defrost time B06A set point-22 degrees and it’s at 30 degrees Defrost times-6 times a day termination 35 min or 47 degrees B06b set point-22 degrees and at 30 degrees Defrost times-was set at one time a day termination time at 35 min and 47 degrees had Sams teach support changed to 6 times a day to match B06A checked out with manager Vivian and explained to her why it iced up | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99793
8/11/2023 10:16:18 AM Toomer, Collin -0001 TT:7:00-10:00 ST:10:00-12:15 Arrived checked in with manager Suman Gained roof access made way to rack c upon arrival found two compressors tripped on high head. Discharge pressure was at 322 upon arrival. Found that 4 out of 8 CFMs not running. Checked VFD and it’s in bypass currently. Checked high voltages at all contactors for the CFMs all getting 481v to each contactor. And getting 124v to the coil. All good Checked fuses for the contactors found two of them motors bad used fuses from the other two motors to get those up and running. Found two motors bad and they where ordered and are at the shop spoke with Jim and we will be replacing next week. After getting two fans back on and running and VFD bypassed discharge pressure is at 216.1psi and suction pressure is at 28.6 Rack C: MODEL TD400 -050 -SC -4 -OHDQ-C REFRIGERANT-R404A SERIAL NO. 0603000645 Call complete will complete repairs on 230730-0210. Checked out with club manager Kristan | Compressors/Motors | Compressors/Motors | 0.99854
Sams Club #6619 -Ontario Systems:DTC-Comp 6 C.S.: 230808-0173 P.O.: 253230762 —————— 8/8/2023 Steve Fierro TT/ST:1330-1430 Time In:1430 Time out:1630 Checked in with MOD Got roof access Located DTC Looked at controller alarms found Primary C06 locked out on oil Located compressor Found sight glass at oil float half way full Reset compressor and monitored run time Checked net oil pressure Checked restriction @ oil separator Sight glass on oil reservoir full Checked for any restrictions at filters/ driers Compressor did not lock out again Tightened connections at contactor and auxiliary they were half a turn loose Call complete | Compressors/Motors | Compressors/Motors | 0.99869
1100am-1300pm (2 hours REG) arrived on site, checked in with britany, found circuit A05 running warm in defrost, called novar found case defrost settings at every 6 hours for 65min, adjusted defrost to 45min every six hours with a 55 defrost temp termination in place. cleaned up work are and checked out with britany. | Nuisance Calls | Nuisance Calls | 0.99834
7/22/2023 1:25:30 PM HERNANDEZ, STEVEN -0001 7/22/23 SH B7 Meat case M-NMG-12 S-4532973 Upon arrival checked in with mod and ivr Located cases on sales floor Found product already pulled Removed deck pans and found case with no frost pattern on valves Gained access to machine room Found LLSV for B7 not pulling any amps Stemmed in solenoid stem for now, to get case to drop while troubleshooting Removed cover and checked voltage at wire nuts No voltage, loosing a leg of power Checked controller and located board and point for circuit Verified RO point closed Traced wires back and found wire had slipped out of wire nut Placed new wire nut Verified solenoid now energized and pulling 10Amps Waited for cases to pull down in temp At departure both 7A/B at 30F and 28F Call complete | Compressors/Motors | Compressors/Motors | 0.99819
Arrived on site checked in went to find door door looked like it got hit cause all the bolts were moved from their place looked at brackets but everything was in tact took the door off and aligned brackets to the main door then adjusted height once we got the door to align we aligned the bumper guards at the bottom for rail to glide smooth tightened everything up and tested door working properly checked out Angel Juarez | Damage by Customer | Damage by Customer | 0.98538
Grocery freezer A5 A4 checked in with mod Found door was open Checked coils for iced build up Do to moisture build up Found iced build up on 2 Evap Forced several defrost Coils cleared up Waited for temps to drop Checked out with mod | Nuisance Calls | Nuisance Calls | 0.99805
Checked in with Heidi, this is not unsatisfactory, the manager did not know why they marked it unsatisfactory since it is running at temp. Temp set-point is 29F and current temp is 30F. Set point for superheat is 6F and current superheat is 6F. Checked history and it shows no signs of high temping since the last time tech was on site. Unit is not in comm loss. Called Novar and confirmed there are no issues currently. MTC09f CASE HUSSMANN MODEL # IC2SM8 SERIAL # MY21G068835 Current temp 30F Let the manager know that the case is working properly and has no history of high temping. Verified with Novar that there are no alarms for this case. Checked out with manager Heidi Call Complete | Nuisance Calls | Nuisance Calls | 0.99839
Completed. Checked in with management. Accessed rack A and found no issues. Checked controller and found all freezers at temperature. The door may have been open for a long period of time during a defrost. Same issue with the snack bar freezer. The door was left open. Freezer maintains 0 degrees when the door is closed. While on site I adjusted the door for POS refrigerator. The door now slides easily. No further issues. | Nuisance Calls | Nuisance Calls | 0.9982
8/8/2023 10:54:27 PM Canadas Garcia, Yelson -0001 I came and checked in with the store manager and I checked the A3 and A4 system and found that the FF2-13 door is damaged, so I sent the information to be quoted and change the new one, the A6a showcases were also checked and the A6b and I found that the door gaskets are damaged, so I also sent the information so that they can order them and come and change them. 9/19/2023 1:03:37 PM Jennings, Jeromy -0002 Job completed I was at the location for another call. Spoke with the MIC Ryan milliff about the door gaskets on the ice cream cases. Unboxed six door gaskets from packaging. Use my pliers to remove six door gaskets on cases a6a and a6b the ice cream cases on the back wall. I use a food grade lube to reinstall the six reach in door gaskets I adjusted two doors so they would close properly. Everything is working correctly at this time. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99708
7/30/2023 6:32:56 PM Paruleski, John -0001 Called for walk in cafe cooler warm Met with manager Amanda on arrival Inspected cafe cooler found fans off and no refrigeration happening. Located a tripped breaker for C1 cafe cooler Reset and got unit back online Inspected condensing unit on rooftop, unit online and running, box is running 40psi, temp is dropping to below 40. All ops check good on departure | Nuisance Calls | Nuisance Calls | 0.9978
8/14/2023 5:56:57 AM Brooks, Byron -0001 Travel: 0830 Time in: 1000 Time out: 1600 arrived at sams club Checked in with MOD assisted lead tech with changing oil controllers for compressor 3 on rack BS and number for on rack B Went inside sams clubs and located bunker A-7 Both boards on sides were off Went to Home Depot and got utilities to fix side panels Fixed side panels Checked out with MOD Call complete | Compressors/Motors | Compressors/Motors | 0.99859
7/20/2023 10:18:01 AM Marchesi, Ryan -0001 2 door break room ric Sams# 0085211 True M#T-35 S#8695634 Arrived on site and checked in with service channel and manager. Found 2 door ric in break room with both gaskets torn. Called local supply house and located gaskets. Placed on will call for me. Will pick up in am and return to install. Notified manager. Follow up. 7/21/2023 12:14:13 PM Marchesi, Ryan -0002 Went to local vendors to pick up gaskets. Drove to store and checked in service channel and with manager. Put gaskets in sun to make them pliable, and take out the wrinkles. Replaced both door gaskets and verified they are sealing. Job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99699
ST:13:30-14:45 Arrived checked in with Loc Found bakery freezer LTA-9 In the back of store Found that the door and the box wall are damaged really bad and the handle is broken. Not all won’t the door to close fully.Spoke with Jose and he advised. KPS comes out and replace door and framing. Spoke with manager he said every time he puts in the call they send us. Spoke with travis, he advised that we need to escalate to another provider KPS to repair the door. No work can be done at this time. No asset tag on the door, can’t find case number other that LTA-9 Job completed. Checked out with Loc | Damage by Customer | Damage by Customer | 0.98642
Found compressor running but showing alarm found wires shorted repaired | Compressors/Motors | Compressors/Motors | 0.99834
8/22/2023 10:44:31 AM Ochoa, Alfredo -0001 082223 Alfredo Receiver level alarm System B Arrived at location and checked in with service channel and store manager. Checked receiver level for rack B and found it at 25%. Called home office to verify and agent stated not only reading low receiver level at -19% but also Al compressors not on and at 0psi. Agent advices to do a power cycle to reset controller. Powered cycle controller and called home office. Agent stated still same readings. Informed agent receiver level at 25%, suction pressure at 20psi and all compressors working. Informed agent novar reading controller not set up yet and still under old controller. Call completed. | Compressors/Motors | Compressors/Motors | 0.99822
Arrived at location, checked in with manager Mark. Proceeded to work on drain pan that is hanging in the walk in cooler that a forklift driver knocked off the evaporator. Took drain pan and straightened it back to normal as best as it can. Need to put new pipe fitting in because the old pipe fitting cracked from fork lift driver. Brazed in the new p trap fitting and put everything back together. Cleared all the condensation ice off of the coil. Drain pan is good to go. Let manager Mark know the resolution. Brand: Heatcraft Model: BMA245AWMSIA Serial: D00L04205 Checked out with manager Mark Call complete | Damage by Customer | Damage by Customer | 0.98457
8/5/2023 Rodriguez, Mateo -0001 Arrived on site and checked in with manager Jeffrey Located system MTB5 meat walk in cooler Both evaporators in walk in leaking water from drain pan Used scissor lift to reach evaporator coil Found drain pan clogged Removed water from drain pan Unclogged using nitrogen Deiced the ice build up on the coil and distributor Did the same to other evaporator Evaporators not leaking anymore Checked out with manager Jeffrey | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99869
7/27/2023 1:28:13 PM Mares, Jeremiah -0001 7/27/2023 Jerry Mares GP# 230726-0370 TN# 251878713 Arrived onsite and checked in with management. Located System A05 ICC running high temp. Found all three cases running above 0 degrees. Case 2 was iced up from a clogged drain line. Removed product and panels to clear drain. Removed all ice from coil. Also removed ice buildup on case 3. Cleaned out trash from cases. Pulled out strainers and inspected. Found strainers on all three valves plugged up as well. Cleaned with degreaser and checked for leaks. Fired up cases and monitored operation. Temperatures dropped, cases maintaining SP. Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
On-site 1000-1545 Arrived on site. Checked in with manager. Made way to roof to check rackE comp1. Comp1 was in high pressure lockout. Reset and compressor is operational. Found one condenser fan motor not running Checked fuses and fuses are good Checked power to contactor and power was present Removed fan guard and checked electrical wiring on motor Found disconnected wire. Repaired wiring and cycled power back to the motor Condenser fan motor is operational and all are running at this time Checked pressures on rack. Suction @ 38psi Discharge @ 289psi A few evap coils are slightly high temping Found 2 coils iced up in the produce cooler Used scissor lift for access Deiced evap coils in produce cooler Monitored temps to ensure they dropped All cases are now at temp All condenser fan motors are operational Receiver level is at 35% All checks okay at this time Job complete | Compressors/Motors | Compressors/Motors | 0.9985
7/28/2023. David Rivera Checked in found ladder made adjustments to curtain return ladder and cleaned up job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99575
7/17/2023 9:48:33 PM Alvarado, Christopher -0001 Arrived to job checked in with manager. Manager showed me location cooler making noise. Found coil b04 and b03 iced up and drain clogged. Washed all ice from coil and cleared drain line with co2. Cooler operating proper at the time. 7/19/2023 4:54:32 AM Garcia, Julian -0002 Assisted tech onsite | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99864
9/20/2023 10:44:13 PM Cosgrove, Reese -0001 On-site 0915-1445 Arrived on site. Checked in with manager. Found rack in comm loss causing evaps to not run through defrost Several evap coils are completely frozen Compressors are also freezing up Receiver level at 0 Reset controller to get comms online Once online called home office to cycle evap coils into defrost Ensured defrost is operational on cases/evaps After running through defrost all ice is thawed out, no longer any ice build up on compressors Monitored to ensure temps drop within range Receiver level is currently at 55 All checks okay at this time Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99773
At site measure strip curtains sent info over to office to get ordered. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99697
8/19/2023 11:43:31 PM Maldonado, Chris -0001 Start time-0045 End time-0115 follow up check in with manager Thomas A. Dodd II checked case B02a product pulled and coils iced up valve turned off manager leavening so I will have to come back tomorrow to de ice checked out with manager Thomas A. Dodd II 8/20/2023 7:53:55 AM Maldonado, Chris -0002 Start time-0800 End time-0930 checked in with manager Al Obregon moved meat products from case MTB-02B MTB-02a MTB-02a running at temp 28.5 took case MTB-02b apart to de-ice turn valve off for refrigeration drain clogged up took co2 to clean it out de-ice coils, opened refrigeration valve back up put case back together, put product back case dropped to 27 degrees set point 28 checked out with manager Al Obregon | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99864
7/22/2023 7:38:39 PM Kapeliela, Kelsey -0001 Arrived on site and checked in with manager Gained roof access, located pharmacy RTU 23, phone system off with high head pressure alarm on the controller, reset system and tested operation, everything came back on, supply temp 51 degrees and zone temperature of 73 degrees on departure Inspected electrical and tested pressure, everything is operating properly at this time, but I did notice that the condenser coil is dirty in need of a wash down and the filters haven’t been changed since July of last year, that service is covered by a separate company Call complete checked out with manager Aaron and notified him on the cleaning of the coil and filters | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99726
7/29/23 Ray Gary Arrived onsite and checked in with the manager (Andrew) Accessed roof and went to Rack room A I found compressor 2 in oil lockout Before I reset the controller I checked for oil leaks and oil levels on the compressor Those were all fine Fired off the compressor and let it run for a period of time to see if it would trip on oil again It didn’t trip So I called Sams Monitoring and spoke with (Ietta)She verified all was good THIS JOB IS COMPLETED ALL PICTURES UPLOADED ON MOBILE TECH | Compressors/Motors | Compressors/Motors | 0.99861
Time in 1500 Time out 1600 Call completed Log into service channel and check in with manager for bs03 high temp -found motor unplug and light unplugged -plugged fan and lights -fan back online case running at set point -ran case thru defrost -case running at set point | Nuisance Calls | Nuisance Calls | 0.99845
7/22/2023 11:04:36 AM Ceja, Mario -0001 Arrived on site checked in with manager and service channel. Located LTA05 bakery freezer . All evap fans running and no ice build up on coil . Called home office temp in walk in freezer is at 0 . Setpoint it at -2 . It reached setpoint serval times today . Walk in door was left open causing high temps . No further issues . Job complete 1130-1200 travel OT 1200-1300 labor OT | Nuisance Calls | Nuisance Calls | 0.99841
WO/COMPLETE..Drove to site logged in with service channel located curb side. Inspected all doors on coolers an freezer in curb side. Adjusted couple doors but when finished associate said they where having issues with emergency exit door. I had to confirm with our service manager he then mentioned we do not work on emergency exit doors. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99682
8/6/2023 12:03:53 PM Johnston, Andrew -0001 Checked in with Matt then began checking rack B. Compressors 1 and 3 are both cycling normally and appear to be running well. Gauged up to each compressor and verified the oil pumps were working correctly. Checked pressure safety settings to ensure they were correct. Checked voltage and amp draw on each compressor and found they were both running well. Verified the compressors had oil in them as well as oil in the reservoir. The rack is running well and maintaining setpoints. Checked out with Matt, call complete. | Compressors/Motors | Compressors/Motors | 0.9986
Travel 1400-1600 Onsite 1600-1830 Will need to quote and order parts Lennox: M# LGE060H4BH2G S# 5605F05889 Compressor: M# ZP54K3E-TFD-130 S# 05CD9044N Liquid line drier: C-163-S Contactor 3pl 40 amp 24v coil 12 lbs of R-410a Recovery charge, welding charge, electrical misc. 2 techs 8 hrs RTU 21 offices and server room-arrived onsite checked in with MOD received roof access located RTU found it with breaker trip ohm out blower motor, condenser motor and compressor and found compressor with open winding and system tested positive for acid will need to replaced compressor, liquid line drier, and contactor will also need to apply acid treatment | Compressors/Motors | Compressors/Motors | 0.99858
8/17/2023 2:54:06 AM Authement, Corey -0001 Head pressure running 325psi found water coil dirty washed coils monitoring, pressure running a at 305 psi on the day time temperature outside 103f will added a water sprinkler due to high out side temps in installed new sprinkler and hoses to help keep head pressure down due to high temps | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99815
8/15/2023 9:18:44 PM Brandau, Kenneth -0001 Arrived at the store logged into Service Channel and spoke with the manager Robert. I looked at rack A and found all compressors working properly photos attached. I spoke to Robert and told him what I found and what I did. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99828
TT 08:00 Time in 08:45 Time out 09:15 Checked out case. Took paneling off in the back. Found that floor drains are clogged for all of meat market . Plumber needs to come out. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99838
GP#230731-0023 0700-1100 TT 1100-1300 RT 1300-1600 RT Drove to Roswell, NM Arrived at store and checked in with the store manager. Working on RTU#15 with no communication for pharmacy area. Found breaker off. Unit off due to a grounded compressor. Disconnected compressor harness and disable cooling. Fan only working. Communication back on unit. Ordered new compressor. Will return to install new compressor and re-enable cooling. | Compressors/Motors | Compressors/Motors | 0.99861
Job is not complete. Need to return to ops of cases once rack pulls down to proper suction pressure. Arrive to store and check in with manager. Gain access to rack and remove all components from compressor and removed compressor from rack. Installed new compressor and pull evacuation on compressor and verified held. Open all service valves. Replace contactor and faulty IDCM board. Pump rack down and replace liquid line drier cores. Start rack and compressor. Begin checking ops and rack now pulling down to proper rack pressure. Found one circuit still running slightly warm possibly due to suction pressure. Will return to verify overall ops of all cases and rack. | Compressors/Motors | Compressors/Motors | 0.99856
Inspected case and found evap drain pan full of water located drain line and cleared drain line with nitrogen tested with water and system drained normally no further issues at this time | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
En Route: 1245 Time In: 1330 Time Out: 1515 MTD Rack Comp 3 L/O Gained access to the roof. All compressors on MTD rack are online. Compressor 3 drawing 17 amps. Rack pressures @ 33/319. No issues found. Job Complete | Compressors/Motors | Compressors/Motors | 0.99855
ST:12:30-15:15 TT:15:15-16:30 OT TT:16:30-18:30 Arrived checked in with Jose Located the meat cooler, after getting lift noticed fan blade busted and the fan was ripped outta place, Was able to use self tapping screw to reinstall fan motor and bracket, installed new fan blade. Tested fan operations. No data tag on the evap coil to be able to get M/S it’s missing. Checked out with Jose | Compressors/Motors | Compressors/Motors | 0.99816
8/1/2023 2:48:22 AM CERDA, JOSE -0001 Found door bent and will only close half way Door gets caught on frame Hinge lifters stuck Opened door 100% and placed lifters in socket All 4 hinges bent Remove 2 bottom hinges Used door to tweak back top 2 hinges Used forklift to run over hinges to flatten back out. Re installed bottom 2 hinges with door in proper location Door now closes Door is bent couple places arent sealed Door frame separating from cooler wall Ask MOD Gatlin if I should quote new door He decided that I should complete call and let club manager make The decision. If door is wanted a new PO will be submitted. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99696
Arrive onsite and checked in with service channel and MOD Hilda. Grab N Go MTC12D HussMann M# ID5SM12 S# MY18H070729 -Found water trapped inside the drain pan -Request to removed all product -Drain hole clogged due from slime dirt -Unclogged using C02 tank. Poured water and drain water good -Grab wipes and towels, cleaned drain pan. Washed and cleaned drain hole protector also -No ice build up in evaporator. Case reached temp set point -Reassemble case and locate manager -Talked to MOD Hilda and showed her what I did. -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99842
Upon arrival found 3 comps off on head pressure. Found all but 1 condenser motor running . Found leg 1 fuse blown on fan motor . Shut rack down and cleaned condenser. Now all comps up and running head pressure at 250 .will order motor and replace once in . | Compressors/Motors | Compressors/Motors | 0.99843
7/26/2023 11:35:24 AM Rodriguez, Johnson -0001 SYS:Rack C Brand:HILLPHOENIX Mod:PS SN:121115 Compressor two dropped by oil was identified, it was reset and left working. I checked voltage and everything is fine. Manager Leo 7/26/2023 11:35:24 AM Rodriguez, Johnson -0001 SYS:Rack C Brand:HILLPHOENIX Mod:PS SN:121115 Compressor two dropped by oil was identified, it was reset and left working. I checked voltage and everything is fine. Manager Leo | Compressors/Motors | Compressors/Motors | 0.99842
Novar needed a new download, once the download was added it cleared the alarms and all cases were operations at proper temperatures. | Nuisance Calls | Nuisance Calls | 0.99725
8/25 RC Replaced parts per pm. Changed filters, oil filter and pressure controls. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.9974
Arrived onsite found BS suction pressure at 85 psi. comp 2 and comp 3 on the BS suction group had no oil in them. reservoir had 2 balls floating. I found plugged up oil filter and also the oil feed line to all compressors smashed. I changed out oil filter and pumped out oil feed line and replaced the damaged oil line. I then got oil to feed back to all the compressors. comp 2 on BS group was still going off on oil. I found a control wire had come off of coil of contactor. I repaired spade and re secured to coil of contactor. I then found The T1 and T3 wires from contactor to compressor only secured to contactor lugs by a single strand of copper. I repaired the wires and resecured back to contactor. All compressors back online. the company thats doing the rack refurbishing is replacing all the compressor controls for this rack at this time. | Compressors/Motors | Compressors/Motors | 0.99856
8/9/2023 5:22:58 AM Moran, Greg -0001 Completed Arrived met with manager.was shown deli case BS04A drain was clogged with old food. Cleared drain and washed out pan. Tested and drain is working properly. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99846
8/15/2023 8:35:42 AM Alcaraz, Jose -0001 TT 0800-0900 Time in 0900 Time out 1030 Call complete Arrived log into service channel and check in with manager for LTA.5 running high temp -found product blocking air -managers were in a meeting waited for them to finish -the manager said a noise was coming from the case last night -had product pulled coil is not ice up and fans are working -manager had case properly restock | Nuisance Calls | Nuisance Calls | 0.99822
Reg Travel:0700-0900 Reg Labor 0900-1130 Lunch: 1130-1200 Reg Labor: 1200-1530 Reg Travel: 1530-1630 Arrived on site, checked in. Located Bakery freezer, bottom of coils frozen and drains frozen, both units are in defrost. Ran into Charles inside store he asked me to check the RTUs around the medium temp cases and redirect the discharge air from RTUs around he medium temp cases because of cases sweating. Located three RTUs 15,16 and 17 that are above the medium temp cases, checked there operation RTU 15 and 17 operating properly. RTU-16 not calling but blower has the VFD bypassed and runs all the time. Went to Bakery freezer and deuces the coil and drain. Cleared drain. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99844
TRAVEL TIME=0 TIME IN=0830 TIME OUT=1300 07/19/23-AARON BIGGS-RACK-B UPON ARRIVAL CHECKED IN WITH MOD JAIME Múltiple SYSTEMS SENDING GHOST ALARMS while actually being at proper temperature. Store is currently undergoing a cutover from SPECTRUM TO OPUS NETWORK. MULTIPLE SYSTEMS ARE NOW ON THE OPUS NETWORK BUT STORE STILL USING SPECTRUM NETWORK SO HOME OFFICE CANT SEE ANYTHING ON THE NEW NETWORK. Will need to get more info on who’s doing the job and when the cutover will be done. Will follow up accordingly after speaking with contractor. | Nuisance Calls | Nuisance Calls | 0.99827
Arrive onsite and checked in with service channel and MOD Judy. LT CU2 Cafe Freezer -Found evaporator ice up front and back -De iced evaporator coil -Checked condenser and has high discharge pressure -No water outlet nearby. Used nitrogen to blew out condenser. Discharge pressure went down to 275psi with suction of 25psi R404a -Monitor the box. Products are a foot away from the discharge air and it prohibits the air flow. Removed product from top shelve and temperature went down to -1f -Locate manager and talked to MOD Judy and showed her what I found -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
Came out and found that the roll up door had been hit and was stuck half way. We had to reprogram the door and then made sure it was full operational afterwards | Damage by Customer | Damage by Customer | 0.9858
7/19/2023 12:55:45 PM Garcia, Julian -0001 Incomplete. Checked in with management upon arrival. Located bs04a with puddle of water underneath. Blew drain line out and poured water to check if line was backed up. Noticed case leaking from corner near frame. Will return tomorrow to reseal corners and edges and recheck. Bs05a and a10a were dry. Will pour water and try to recreate leak and resolve. 7/21/2023 5:03:38 AM Garcia, Julian -0002 Complete. Checked in with management upon arrival. Checked bs04a and was still leaking. Resealed and caulked inside of case and left to dry. Checked Bs05a and a10a and located leak. Asked to have product moved and cleared racks and covers. Found clogged screen around drain. Removed screen and standing water drained. Cleaned and rinsed screen and blew out drain with compressed air. Poured water and drain was clear. Saw no leak. Returned to bs04a and poured water and notice case was still leaking. Removed metal bumper guard and from trim piece. Noticed water was leaking all across back of case behind evaporator. Panels are old separating due to age of case. Recommend to manager case should be replaced. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99492
8/10/2023 10:09:03 AM Stuart, Christopher -0001 En Route: 0730 Time In: 0900 Time Out: 1200 CPU Freezer Running Warm (Home Office Call) Checked into Service Channel Checked in w/MOD Katrina Kysor Warren (CPU Freezer) M# FX5SL-03RUN S# C17H00393 R-404a Located CPU freezer. Case controller displaying an ER 7 alarm and case temp at 59. Removed deck pans and the fans were not running. Slight ice build up on distribution, suction line and in the middle of the coil. Put unit into manual defrost and de-iced coil with hot water. Put case back together and terminated defrost. Case temp got down to -2 after about an hour. Set point is -6. CPU freezer is right next to two exit doors, and constant opening and closing the doors let’s large amount of warm air into the case and ices up the coil. Adjusted defrost parameters for the freezer. Defrost will Now occur once every 12 hours, for 45 minutes per. Increased drip time to 3 minutes defrost term temp to 50. Checked out w/MOD Katrina Checked out of Service Channel Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99866
7/23/2023 3:58:12 PM Quezada, Arturo -0002 Checked in with manger located RTU walking Checked all pressures and defrost times Employee called it in as emergency when it was on defrost Everything is good. Job completed | Nuisance Calls | Nuisance Calls | 0.99828
7/14/2023 2:11:14 AM Martinez, Alexis -0001 Checked in with Amanda Checked out with Amanda Reason for call: self contain high temping Unit: KYSOR WARREN Model: FX5SN -03RUN Serial: C17H00391 Upon arrival self contain was temping at 30 upon arrival Checked for air flow and ensured coil had no ice build up Temp thermometer was reading air flow at 29 Noticed dirty condenser coil Grabbed nitrogen and cleared condenser coil and fan Used meter to check amp draw -amp reading 5.1 Connected gauges to gather head pressure Head pressure while running was 260 Checked start capacitor with meter -Read at 80.6 micofarads -within proper operating range of 72-88 Monitored unit while checking operations unit continued to meet set point with out fail Checked wiring to ensure proper connection was being made Found no issues with unit Call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99735
Found condenser fuse on disconnect bad. I replaced fuse with another 60amp fuse I found in the condenser. I checked amps L1 is 27amps L2 is 32amps and L3 is 32amps. Cases are now cooling properly. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99696
Start time-0845 End time-1500 complete checked in with manager Sabine pulled product pulled case apart to find broken fan, coils iced up turned the valve off to defrost went to united for new fan put new fan in and finished de-iceing checked out with manager Sabine | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9986
EnRoute: 8:00 Time In: 10:00 Time Out: 11:15 Rack A Arrived on site and checked in with Service Channel. Climbed on top of rack and found all condenser fans to be running. Checked rack B and C and all fans were running as well. Got with the team to see who changed it and found out David changed it on separate ticket. Call is complete | Nuisance Calls | Nuisance Calls | 0.99828
Sam Club #: 6624 System: A07/A06a SC: 230819-0244 PO: 254177116 —————— 8/21/23 Kenneth St.Amant Travel-06:00-08:00 Onsite-08:00-16:30 Checked in with manager Arrived on site checked in with location gained access. Bakery freezer coil was a little frost on them so I put into defrost and I all the frost is gone The defrost terminate temperature was set to high at 70 so call home office and had them change the defrost terminate temperature to 55 Bakery freezer back at temperature The gate to get in the motor room had no lock or chain so when to Home Depot for a new lock and chain A06a took case apart and it was really ice up in the back of the coil There was trash and there was a trash in the back of the coil blocking the water to it ice up due for the trash blocking the water Put case back together and it at temperature Checked out with manager Markeith Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99849
8/4/2023 6:50:00 AM Carrasco, Earnest -0001 Job is not complete. Have compressor and all parts needed arriving to united Brookhill on 8/7/23. Parts coming from Dallas. Arrive to store and check in with manager. Locate rack and found suction pressure running high. Check and verified all compressors online. Found BS1 off on digital scroll module for high discharge temp. Felt end bell of compressor and found extremely hot. Try pumping compressor down and valves will not hold. Call united and compressor with not be in until the 7th. Will return to install once parts arrive. Rack maintaining suction pressure for time being. 8/10/2023 4:55:23 PM Carrasco, Earnest -0002 Job is not complete. Need to return to ops of cases once rack pulls down to proper suction pressure. Arrive to store and check in with manager. Gain access to rack and remove all components from compressor and removed compressor from rack. Installed new compressor and pull evacuation on compressor and verified held. Open all service valves. Replace contactor and faulty IDCM board. Pump rack down and replace liquid line drier cores. Start rack and compressor. Begin checking ops and rack now pulling down to proper rack pressure. Found one circuit still running slightly warm possibly due to suction pressure. Will return to verify overall ops of all cases and rack. 8/13/2023 9:16:57 AM Carrasco, Earnest -0004 Job is not complete. Need to pick up new case controller and LCD screen from united refrigeration and return to install. Sensor was used from Nick M inventory. Please remove CDS valve from ticket and move to truck stock. Arrive to store and check in with manager. Locate case and found case running at temp. Begin checking ops and found case controller broken and possibly causing case to go in and out of temp. Also, did find sensor going in and out and reading off by 12 degrees. Replace sensor and case now reading proper temp. Will return to install. While on site found LCD for rack B inside of store not working. Contact novar and was told to replace LCD, will also pick up from united ref. All other cases are at temp at this time. 8/28/2023 4:18:40 PM Ramirez, Julio -0006 Job is complete Was at store for another call. Located rack B exterior of store. Pumped down compressor .Isolated compressor B1 and removed discharge thermal. Installed new thermal and evacuated compressor. De isolated and energized compressor. Monitor to make sure compressor running like normal. | Compressors/Motors | Compressors/Motors | 0.99844
8/2/2023 4:20:02 PM Gonzalez, Steven -0001 In 08:00 out 11:30 Checked in with Maryann Working on freezer door not closing properly Checked door and found door is bent damaged by forklift Found door gasket starting to tear will need to be replaced Also found outside door handle damaged and starting to come loose will need to replace Also trim on door is damaged and needs to be replaced Will order all parts and replace The door is pretty damaged and bent is part replacement does not fix problem we may need to replace door follow up required 10/17/2023 4:36:13 PM Ortega, Uriel -0004 GP#230801-0372 Checked in with store manager. Working on replacing 6x9 freezer door. Removed all forklift guards to access door. Uninstalled damaged door and took to warehouse. Unpacked new door at warehouse receiving area. Moved new door to walk-in freezer and installed. Mounted all hardware from old door. Door handle broken. Performed a temporary repair on handle. Need to order new door handle. 12/4/2023 8:22:39 PM De la Cruz, Adrian -0006 12-4-2023 Adrian De La Cruz Jr GP# -230801-0372 PO# -252504701 1700 -1730 TT 1730 -1900 on-site Checked in with store manger Amy Rhea. Located freezer door handle that needed to be replaced because it was damaged. We took off the damaged door handle parts and replaced them with the new door handle parts that we got ordered in back home in El Paso. Me and my partner coordinated taking it apart and putting it back together properly on the freezer door. When we were done we tested the new installed freezer door handle to make sure it was opening and closing correctly. -Job complete 12/6/2023 9:08:36 PM Shimel, Richard -0007 Assisted Adrian on call Checked in with store manger Amy Rhea. Located freezer door handle that needed to be replaced because it was damaged. We took off the damaged door handle parts and replaced them with the new door handle parts that we got ordered in back home in El Paso. Me and my partner coordinated taking it apart and putting it back together properly on the freezer door. When we were done we tested the new installed freezer door handle to make sure it was opening and closing correctly. -Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99672
Follow up needed 8-17 Arrived on site checked in found rack reading at 0 percent at time I pumped down the rack and it was low I went and leak checked down stairs on the cases and had the store assist in checking above the coolers and found nothing I then went back up to the rack and started to leak check I found compressor number 2 leaking from the liquid injection line pictures attached I went and ahead and valved compressor off and when I went to loosed the fittings I was able to just twist it off w my hand I put some leaklock and turned the compressor back on its no longer leaking will return and check to see liq level checked out with Cody | Compressors/Motors | Compressors/Motors | 0.99824
Job is complete Arrived at store. Checked in with manager. Located case MTB-10e on sales floor. One side of case had no airflow. Went ahead and cleared product to remove bottom panels. Once removed saw that drain was clogged and case had standing water. Also due to water one of the fan went out. Went ahead and cleared drain clog and made sure it drained to flor drain. isolated old motor and removed and installed new motor. Energized new motor to make sure rotation is good and good airflow on top of case. Checked to make sure case temp dropped and maintained temp. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99824
MT2 grab n go case by cafe leaking water. Hussmann ID5SM6 MY19E038929 On site already. Asked to get product pulled from bottom shelf. Found case drain clogged. Cleared with co2. Found water stuck underneath both plenums. Closed off hand valve and unplugged fans. Cleaned case with hot water and remove all slime and trash from case. Cleared with co2 again. Put case back together. Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99847
7/24/2023 6:15:20 PM Marchesi, Ryan -0001 Sys MTB-s4f On site. Checked in service channel. Found floor sink for island m/d cases plugged and overflowing. Removed guard rails and toe kicks. Screen for sink was plugged full of slime. Dumped and cleaned out in mop room. Cleared floor sink with co2 and rinsed with buckets of hot water. Mopped up as much water as I could. Put back toe kicks and rails. Checked and found other floor sink on the island plugged up as well. Cleaned and rinsed with buckets of hot water. Cleaned up water from floor. Informed manager of findings and that there is still a small amount of water under cases that will need to dry. Job is complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99772
7/13/2023 9:37:45 PM Garreans, David -0001 TTOT 2145-2215 Time in 2215 Time out 2300 Checked temperatures on rack first. BS01 bakery cooler is at temperature of 32 degrees. Snack bar cooler is at 35 degrees. No issues found. No alarms in historical 1 day of alarms at all for either of these circuits. Myself and manager Latryse Francis walked to bakery walk in and cafe walk in and visually inspected temperatures. All were at proper temperature. No issues found. Complete | Nuisance Calls | Nuisance Calls | 0.99798
7/25/2023 9:30:54 PM Porrata, Favian -0001 Upon arrival checked in with Manager Peter. Call was for Ac by check is not blowing. When doing my inspection of the Ac unit. Check split and and a 24 split. Check to make sure all compressors where on. Made sure all condenser fans where running. Checked pressures. Everything checked ac is running. Call complete. | Nuisance Calls | Nuisance Calls | 0.99815
Duplicate of 230730-0197 | Nuisance Calls | Nuisance Calls | 0.99772
8/14/2023 2:53:41 PM Stuart, Christopher -0001 Time In: 1330 Time Out: 1430 B1.1 MD Produce Hi Temp (Home Office Call) Case temp at 37 on arrival, with a set point of 31. Removed some product, deck pans and accessed the evap coil. The coil was slightly iced up and both fans were operational. Found oil stains below the TXV. Leak checked and the TXV screen was slightly loose. Tightened the screen and the leak was sealed. Removed small ice build up with hot water. Accessed Rack B. Sight glass solid, receiver at 25%. Checked defrost parameters, and the case has 6 defrosts with a term temp of 47. Called Home Office and had them change the defrost term priority to duration to allow case to have full defrost cycles. Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
call is the same as TN: 253288619WO#230809-0031 Checked in with Erik, went ahead and walked through the store, all the cases are good on temps, on cases C05 a and B, looked to be at 35 degrees, came outside to the rack house and checked the Sporlan control and the temps its showing is 35 and 30 degrees. I checked all systems on rack C, everything is on temp ranging from 28-32 degrees. Talked to Erik and checked out. | Nuisance Calls | Nuisance Calls | 0.99837
8/3/2023 8:09:09 PM Lopez, Noe -0001 08/03/23 Noe Lopez System: S/C Case MT -Checked in with MOD -Went to inspect case noticed airflow was hot -Went to inspect the compressor and condenser fan -Both were off -Went to check the compressor 3 legs all showing compressor was in good standings -Checked wire 23 for the leg that feeds the compressor and start up -Red wire that was only pulling 20 volts -Conducted a wire trace to see where the breaker was attached -Traced the wire to breaker LD4 on 39 -Tried to pull breaker to on position, breaker would not pull to on -Informed manager to call in a electrician to repair breaker -Per management she informed me that she would have him put the wire that is currently on 14 need it back on 23 when done -Amperage on 14 is currently 6 -Job complete | Compressors/Motors | Compressors/Motors | 0.99864
Anthony Robak Checked in with Fernando Went to rack c to check monitor for club pickup case LT-SCa. IC Found case at -4.8 degrees Found case C6 at 31 degrees Called home office and confirmed case C6 was at 49 degrees during defrost at time of call Both cases at temp Will return in am to check ops on case LT-SCa Staff is gone for the night follow up | Nuisance Calls | Nuisance Calls | 0.99818
7/27/2023 12:54:20 PM Delgado, Fidencio -0001 Arrived on site checked in mod CHRIS and service channel. Proceeded to rack C. On arrival found all compressors on line and 1 was running not off on oil. No alarms on opus. Checked amps compressors amps good. Called sams club home office spoke with IDIA and also said she sees no alarms form rack C for compressor off on oil. Looks like false alarm everything up and running . Checked out mod CHRIS and service channel. JOB COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99824
Time in 0900 time out 1530 Arrives on-site checked in with manager went to roof found unit cooling. Called monitoring and they showed temperature in office was 77 set at 74. Washed condenser coils. Checked evaporator and was a little dirty. Brushed off evaporator. Turned unit back on. Unit started cooling. Watch temp come down. Zone temp is at 73 degrees call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99739
7/20/2023. David Rivera checked in found fan not working. Went to get lift took guard off and fan . Went to get parts came back and installed the fan and cleaned up . Job is completed | Compressors/Motors | Compressors/Motors | 0.99779
Arrive onsite and checked in with service channel but the tracking number is closed. Checked in with MOD Serked A05 & A06 -Checked the circuit and it is cooling properly. A05 just got out of defrost and temperature is coming down close to the set point. Checked all the product and they are frozen -Went to the rack house and no issue found. No alarm for these circuits. Sight glass clear and receiver level at 35% -Searched history. Repair is complete. Refer to WO 230824-0210 -Locate manager and talked to MOD Serked and explained what I did -Job complete | Nuisance Calls | Nuisance Calls | 0.99836
9/12/2023 9:24:53 AM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Serked Rack B Compressor 4 -Compressor 4 offline. Troubleshoot wiring -Found compressor contactor coil connector loose -Connect and secure connector -Monitor and compressor back online. -Locate manager and talked to MOD Serked and explained what I did -Job complete. | Compressors/Motors | Compressors/Motors | 0.99865
7/31/2023 11:26:23 AM Davila Garcia, Pedro -0001 Duplicate of 230730-0197 | Nuisance Calls | Nuisance Calls | 0.99768
15 Jul 25, 2023 MST Created By Miguel Jaquez PMC Southwest Work Summary: Arrived on-site checked in with management gained access to rack MTC checked controller found compressor 12 off on oil. Found both compressors with oil checked contactors for compressor 1 and 2 both contactors were burnt. Replaced contactors performed pump down test on compressors found oil filter in separator plugged partnered with monitoring to suppress alarms for rack c isolated discharge line and recovered refrigerant from discharge line removed existing filter and replaced. Also replaced OFE-1 filter and cleaned strainer on oil differential valve vacuumed isolated discharge line opened lines checked operation 8/15/2023 Jaquez, Miguel -0002 Arrived on-site checked in with management checked rack MTC compressors 1 and 2 found both compressors operation noticed compressor 3 had pitted contactor went ahead and shut compressor 3 off installed new co factor checked operation all compressors are working properly at this time. | Compressors/Motors | Compressors/Motors | 0.99856
de-iced dairy WI box coil. checked and adjusted SH and confirmed valve screens are clean. SH was at 2° raised it to 10° system is operating OK also confirmed defrost operation. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
dairy WI coil is slightly iced up. Will need to return to deice and diagnose issues. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99832
8/11/2023 4:42:40 PM Schwab, Justin -0001 Found rack off on high head and tripped vfd. Repaired short and reset vfd, fans are on. Comp 2 has a new current sensing relay ordered. | Compressors/Motors | Compressors/Motors | 0.99837
Make: Heatcraft Model: LET047BK Serial: D03A06987 Unit: MT1 -upon arrival case was at 40f with evap coil iced up and drain froze over -checked system and forced defrost and defrost works. I then decided coil and system was diagnosed with a bad defrost timer. -I picked up defrost timer from United then returned and installed and rewired to match newer model defrost. Timer was set for 30 minutes 4 times a day as previous timer. -reassembled system and turned system back on. Case pulled down to temp. No other issues system operational. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
07/14/23ZP SAMS CLUB 4703 System MTB2b -Got access to the WIC -Requested for product to be removed from shelving. -Got access to the coil and found water build up. -Removed union and water began to drain. Put the drain back together -Went to get a 5 gallon bucket. -Began to drain the water from the drain pan. -Empty water and began to drain remaining water. -Cleaned up water -Located the mod and informed them of the situation -This call is now complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99845
8/4/2023 6:42:00 PM DeBeaulieau, Andrew -0001 Kysor-Warren OIV5V14-03UN 0809001756 Checked in with service channel. Shown case A-5C reach on frozen food. Case is iced up, turned off liquid line hand valve. Had home office initiate defrost. Defrost heaters 5.7 amps Pulled case apart to deice, found 2 defrost heaters unplugged behind fans. Plugged in heaters and Deiced coil. Heaters now 8.7 amps and individual heaters that were unplugged now drawing 2.9amps each. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
7/31/2023 11:21:56 AM Davila Garcia, Pedro -0001 Already on-site previous work order after check operation found the defrost schedule have two defrost per day instead four defrost per day. I call monitoring and fix the issues now case A9.4 and A9.5 have 4 defrost per day | Nuisance Calls | Nuisance Calls | 0.99837
7/31/2023 6:27:14 AM Cosgrove, Reese -0001 On-site 0930-1245 Arrived on site. Checked in with manager, Brad. Found ice cream freezer high temping Removed product to inspect evap coil Found evap coils frozen Deiced evap coils until all ice was thawed. Cycled system through defrost Defrost cycle was not working for a03b Found wire for heater burnt and disconnected Cleaned up wire, reconnected with wire nut. Cycled through defrost and confirmed operations Monitored freezers to ensure temps dropped within range Freezers we’re all below 0° before tech left Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99862
Checked in with manager Julie, the compressors are tripping on oil. The oil pressure is off on the whole rack, so the rack needs a whole compressor oil change and filter clean. The cases are at temp now but it will trip on oil, the oil is black. compressors 3 and 4 are running without interruption however this rack needs a full oil change. RACK B MODEL #PS425SMRAD SERIAL # 25417-129 Compressor 3 MODEL # 06DM3370DA3650 SERIAL # 6DKERC4R2J41 COMPRESSOR 4 MODEL # 06EM775600 SERIAL # 6EBCBD1E2C41 Let the manager know that they need to place a work order to do a whole rack oil change, the oil looks black in the sight glass and compressors keep tripping on oil. The rack is no longer in lock out and all the compressors are running. Checked out with manager Julie Call Complete | Compressors/Motors | Compressors/Motors | 0.9986
TIME: Overtime 1700 to 1730, 0.5hr Overtime travel 1730 to 1915, 1.75hr DESCRIPTION: Checked in with store manager. Checked the assignment comparing the Asset numbers, and realized that this ticket was duplicated, because another tech Jeremy commented the job today with a helper tech. So the job was completed by another tech Jeremy and his helper today. | Nuisance Calls | Nuisance Calls | 0.99833
8/24/2023 4:39:54 PM Immoos, Jesse -0001 B5c Hussman M# F-8G S# MY22G070125 Found no air flow at at honeycombs. Connected to case with Sporlan app, found temp at 37°, set point 22°. Alarm for incomplete defrost. Graphed temps found average climbed last 5 days. Graphed cases A and B on circuit on lcd at rack. Found they have been at set point the last 5 days. Had product pulled found both fans working, coil with frost build up. Forced defrost at case found heaters getting 0V. Removed bumper guards and dropped control panel. Traced defrost wires to breaker. Breaker with 0V, relay with 0V, and found 208v at terminal. Had to cut all zip ties and check all wires, found loose wire at terminal. Pulled fuses at rack to defrost circuits and placed wire back on terminal. Forced defrost and found heaters pull correct amps. Forced defrost and frost cleared. Case with good air flow and pulled to set point. Call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99822
7/24/2023 8:04:02 AM Hanamornsate, Thirathanawat -0001 7/24/23 TH TT: 8:00-9:00 Time in: 9:00 Time out: 10:00 MTC-6a: Meat prep Heatcraft MN: WK155AC SN: D06D03308 MTC-06b: Heatcraft MN: WK155AC SN: D06D03307 Checked in with Service channel and MOD (Marcus). Checked the location and both coils are clean and good airflow. Checked Suction and Discharge pressure are good. Checked the temperature and both units are good temperature. Set point is 43 degrees F and both unit are 44 and 45 degrees F. No Alarm present. No found issues. Informed and checked out with MOD(Marcus) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99838
8/01/23 06EZ7753GARP 3222GE2568 -Arrived on site and checked in with MOD and into service channel. -Accessed motor room and found rack MTB. -Suction psi between 58-62 upon arrival, cut-in setpoint at 56psi. -Verified suction pressure at transducer, 62psi. -Found one compressor toggled off and labeled “bad compressor”. -Rack needs all compressors online to get to suction pressure. -Will need a quote for compressor, contactor and auxiliary, low & high pressure switches, 2 techs, 10hrs each. -F/u to r/r compressor. -Job incomplete. | Compressors/Motors | Compressors/Motors | 0.99861
Found compressor 1 on rack A tripped on high head. All fan motors are currently running on A rack. Discharge pressure is reaching 340 during the heat of the day. I highly recommend changing out the condensers on A and B rack. They are deteriorating. Reset compressor and it came back online. All compressors are currently running. Adjusted the head pressure control on comp 1 also. It was set at 300 and I moved it up to 375psi. Compressor stayed running. Discharge is currently 305psi. Washed out condenser and it helped a little bit. Condenser really needs to be replaced. | Capital Replacement | Capital Replacement | 0.98525
Jul 21, 2023 Replaced bottom guide rail for sliding POS freezer door. Door is now staying in the track. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9971
7/31/2023 7:36:31 PM Frietze, Robert -0001 LTA-2/3 Walk In Freezer Door 7/31/2023 Robert F Dylan L Upon arrival checked into ivr and with mod. Accessed first walk in freezer and found door rubbing on floor and jamb gaskets on sides damaged. Also stay rollers not in proper position for door to close and seal properly. Found door on handle side with metal coming apart and catching on gaskets. Removed damaged jamb gaskets and raised door up to stop rubbing on floor. Repaired door metal damage and installed new side jamb gaskets with pointer screws. Then adjusted stay roller on left side of door. Then had to move stay roller on handle side to a better position (used one concrete anchor). Then adjusted stay roller for proper closing. Then added a guide spacer to prevent door from hitting left side jamb gaskets every time door is opened or closed. Cleaned work area job complete. 7/31/2023 8:23:36 PM Lopez-Castro, Dylan -0002 Walk in frozen door. 07/31/2023 Dylan Lopez Arrived on site checked in and out with manager and service channel help assist tech on what needed to be done. See lead techs notes. Call complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99712
Replaced shorted compressor. Pulled vacuum, and recharged to factory specifications. Let run to set point of 29°. | Compressors/Motors | Compressors/Motors | 0.99859
8/17 Checked in with manager. Upon arrival I found that all of rack MTC was down due to com loss and network failure. I spent 3-4 hours on the phone with sams club/novar reprogramming controls and re-syncing all circuits that were out on com loss. Also found that the defrost schedule was set on all circuits on mtc to 6 times a day with terminations temps set to 55 degrees and defrost length was set at 40 minutes for each defrost. Had sams club program defrost to 4 times a day for 30 minutes with a defrost termination temp at 45 degrees. Was able to get rack back up and running and made sure all circuits were reaching set-points. Once all compressor came back on I was having issues with liquid flood-back to the compressors. Due to rack being down for so long it caused liquid to stack in the oil reservoir causing compressors to go out on oil failure. Got on the phone with David G. To get some insight on getting liquid out of oil reservoir. He had me isolate compressor 3 which was the main compressor having the most liquid flood back. I allowed comp 1&4 to cycle refrigerant through the system and was eventually able to remove the liquid from oil reservoir and out of compressors. Opened valves back up on comp 3 and allowed system to run for an hour to ensure there would not be anymore oil failures or issues with high temps at the circuits. David wants me to put in a follow up for him and myself to return this following Monday 8/21 to go back over rack and system operations. | Compressors/Motors | Compressors/Motors | 0.99846
Incomplete, Parts on order. Checked in on site. Located walk-in needing services. Used ladder to disconnect fan & remove fan cover. Fan adjusted to minimize noise, cover re-installed. measured walk-in curtains and filled form and sent to willie to order parts. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99597
7/28/2023 10:12:48 AM Kurth, William -0002 Arrived on location checked in with the manager she information me that JO was out two days ago for rack A comp 5 lock out I gained access to the rack house and found comp A1 locked out on oil with oil in the reservoir I reset the oil safety and watched the compressor run it showed no signs of oil issues during operation sitting with in recommend oil levels per manufacturer specs I performed a pump down test on the compressor and found no issues I did find flood back to comp A5 which receded once a system went into defrost so I cleaned up and locked up the rack house I did a quick scan over all the refrigeration equipment to verify there was no other issues I informed the manager and I gave here the tracking number for this call so she is aware what I looked over and checked out call complete | Compressors/Motors | Compressors/Motors | 0.9984
7/20/2023 12:59:56 PM Floyd, Kaden -0001 Arrived to store let the manager know I was here to take a look at the look tow fan motors not running in the meat cooler walk in I then went to the cooler I got the scissor lift I got to the motors I saw the power off to all the motors I then looked and saw the fan blades were bent enough to where the wouldn’t spin so I went to united refrigeration I got one new fan blade cause that’s all they had I installed it and bent one of the old blades good enough to where it’ll work and move air I then turned the motors back on and there all running 7/20/2023 5:36:29 PM Floyd, Jimmy -0002 Kaden replaced fan blade in meat cooler I’m just consuming parts | Compressors/Motors | Compressors/Motors | 0.99786
Arrived at meat department removed panels water was about 2 inches deep in the case had to get some CO2 from United and clear out the drain Drain cleared and case cleaned Leak repaired | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99845
7/20/2023 8:16:57 AM Dearing, Lyndon -0001 Checked in with mod. RCU 3 not cooling Checked unit and found it off on high head pressure switch. Reset unit and checked pressures pressure is within range unit tripped on high head due to record high ambient temperature | Nuisance Calls | Nuisance Calls | 0.99763
1100-1145 Called out for meat case B06a warm Met with manager Jen Inspected and found case iced up Had product pulled, shut hand valve off. F/u in AM to restart. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99829
Checked in with Corey. Let him know I will be deicing the drain pan in the POS cooler for unit #2. Got my tools and trash can with sump pump out of my van. Set up the hoses and sump pump. Went to get hot water in the trash can. Could not get a scissor lift in there so I got a ladder and went to check out what was going on. I melted off the ice right where the drain hole was so all the water will go away faster. Noticed that the water was not going away so I checked the drain hole to see if it was plugged. There was nothing blocking the hole so I took apart the pipe for the drain. Once the pipe was out I saw there was a lot of slime/dirt so I cleaned it all out. Put the pipe back on and continued to deice the pan. After all of the ice was gone I also cleaned the evaporator coils with nitrogen and sprayed it with water as well. Cleaned up the area and put everything away. Checked out with Corey. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99847
TTOT 2145-2215 Time in 2215 Time out 2300 Checked temperatures on rack first. BS01 bakery cooler is at temperature of 32 degrees. Snack bar cooler is at 35 degrees. No issues found. No alarms in historical 1 day of alarms at all for either of these circuits. Myself and manager Latryse Francis walked to bakery walk in and cafe walk in and visually inspected temperatures. All were at proper temperature. No issues found. Complete | Nuisance Calls | Nuisance Calls | 0.99801
Favian Porrata 07-25-23 Arrival 1445 Departure 1545 Upon arrival checked in with Manager Peter. Call was for no water in the tire center swamp cooler. Started off by access swamp cooler. Started to do my inspection and found the swamp cooler to be on but water to be off. Made sure pump was good. Than check to make sure water float was also good. Than found the water line to be shut off. Turned water line back on and swamp cooler back on. Swap cooler is now cooling. Notice float is old and not stop at full line will need to replace. Will return to install part. Call incomplete. | Capital Replacement | Capital Replacement | 0.98656
Travel 0600 Time in 0630 Time out 1900 Rack C compressor 4 New Bitzer Comp Model #: 4FTE-20-2NU-00 Serial #: 2504713763 Follow up to replace Bitzer comp. Used crane to bring down old comp and bring up new compressor. Left old compressor at Sam’s club to return for warranty. Suction pressure reaching setpoint now. CALL COMPLETE | Compressors/Motors | Compressors/Motors | 0.99855
8/3/2023 6:09:19 PM Zaun, Paul -0001 8-3-23 Paul Z / fan making noise Kyser warn S# C19m00156 Checked in with Thomas removed product from case found case is full of water and fan blade is slapping water cleared drain with co2 debris was released from case case is clear of water Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
8/2/2023 7:02:41 PM Alcaraz, Jose -0001 TT 1030-1430 Time in 1430 Time out 1700 Call complete Arrived check in with manager for server room and manager office hot -found RTU running high pressure due to extreme heat and dirty condenser -went to Home Depot picked 400 feet of water hose -ran hoses across the roof and cleaned condensers -drop head pressure -called home office they said RTU are in comm loss -reset controller got communication restored -left hoses on site | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99752
Sams 6686 Salt Lake 11-21-23 Service call 230718-0579 PO 251259687 Comp B 1 replacement TT/ST 0745-0815 ST 0815-1345 Returned to store with parts Replaced compressor B1 Replacd Contactor Replaced auxiliary switch Pumped in 1 gallon of poe 68 Leak checked with bubbles Let compressor run 2nd Leak check electronic sniffer No leaks found Compressor running between 7 and 8 amps On each leg Checked ops OK Took old Compressor for core return | Compressors/Motors | Compressors/Motors | 0.9986
Service channel would not allow me to login. I am in the process of having to correct this. I checked in with the manager about this call because of the lack of service channel access. The prep table had been shut off on my arrival with the thermostat disconnected. I reconnected the thermostat turned the unit back on. It began to run. I opened the panels and carefully inspected the electrical connections. I noticed that the condenser coil was extremely dirty so carefully blew it out with nitrogen. I then attached my gauges to the service ports and observed the refrigerant levels and pressures. After careful observation the unit appeared to be functioning normally and have the proper charge. By cleaning the coil I lowered the pressure on the unit. I returned the next morning and checked on the unit once more using gauges and thermostats. The unit is running normally now. | Nuisance Calls | Nuisance Calls | 0.99833
7/14/2023 5:34:42 PM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Cathy LTA 5 SD Meat HussMann M# F-12G S# MY18H064791 -Checked air flow, low air flow -Request removed all product. Found evaporator fan motor not working due main power plug loose -Grab trash can and water pump. De iced coil -Run defrost and heat element reads 5amps -Monitor case temperature and reached temperature set point of 32f -Locate a manager and talked to MOD Hilda -Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
8/18/2023 7:09:17 PM Chapman, Blake -0001 Upon arrival rtu-10 would cycle on and then cycle off after about 16 seconds. The code showing on the display was indicating that it wasn’t calling for the fan blower motor to come on, this was leading me to believe that someone put the fan on the thermostat to the off position. I couldn’t gain access into the pharmacy due to safety regulations. | Nuisance Calls | Nuisance Calls | 0.9982
I came and checked in with the store manager and checked the A2 compressor and found that it was protected by the oil switch, so I reset it and the oil pressure differential and suction pressure tests were done and it was within normal limits but the oil receiver was completely empty, so I went to buy the oil and the oil filter and I changed the oil filter and the receiver has two full sight glasses and it works inside normal | Compressors/Motors | Compressors/Motors | 0.99863
8/12/23 Sam’s club 6613 Rack MTC Comp4 Oil Lockout Alex Medina arrived on site, checked in on IVR and MOD Hector. Obtained roof access for rack MTC. Headed to rack. Confirmed comp 4 off on oil on controller. All other comp SG half full and running. Checked comp 4 oil SG and found it to be half full. SG had a mixture of yellow and white indicating possible liquid in comp. Isolated compressor and pumped out liquid from comp. Opened comp up and ensured SG filled up. Cleared alarm for comp 4 and started it up. Comp making a loud humming noise. Clamped up and comp is pulling 166 amps. Comp is locked up and will need to be replaced. Will need to get compressor under warranty. Rack suction high @ 480# with a setpoint of 427#. Did a store walk around and found that cases under rack C are in the low-to-mid 30’s. Cases maintaining temp for the time being. Informed MOD hector. CALL NOT COMPLETE, COMP 4 NEEDS TO BE REPLACED. | Compressors/Motors | Compressors/Motors | 0.99836
Checked in Jeremy about a follow up on Freezer Door, Door is missing door stop and a it looks like a sensor, we let Jeremy know that parts will have to be ordered , will order parts with Lawrence, we told Jeremy we would give him ETA on parts once we get that from Lawrence. Call Incomplete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99719
7/25/2023 Pena, Daniel -0001 Arrived on site checked in with manager service channel Found Dairy RCU3 at 55 Asked for roof access found RCU3offline Found breaker tripped Look for any shorts on Checked Compressor if ground it’s not grounded Checked windings okay Found contactor for Compressor pivoted Went To supply to pick up needed contactor RR Contactor Restarted RCU Monitored opps Dropped to set point Call complete | Compressors/Motors | Compressors/Motors | 0.99868
8/8/2023 5:08:10 PM Jennings, Jeromy -0001 Job completed Arrived on site for a bakery cooler freezer door, not closing correctly. I adjusted the striker where the door would close and stay closed and everything is working fine at this time. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99713
Start time-1530 End time-2200 complete checked in with manager Michael Hooper asked manager to move product leaking from LTA-6 broke up ice on the floor and dumped it out side broke up ice in drain pan plastic in drain pan, cleared drain with co2 test drain with gal of water replaced old drain pan with new drain pan (Jose will email Sheena and Sarah on Aug-4-23 for price of drain pan) put case in defrost to make sure heaters work (all hearts working) de-ice coil and txv cleaned up water and ice from floor and shelves checked out with manager Michael Hooper | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9986
7/27/2023 2:02:34 PM Delgado, Fidencio -0001 Arrived on site checked in mod CHRIS and service channel. Proceeded to WIC found temp at 21 degrees too cold. Wic controlled by pressure, found preusre control set to 50 which converts to 18 degree coil. Moved up to 60 which concerts to 23 coil temp. Let system run a few cycles te.p after adjustment 38 degrees. Checked out mod CHRIS and service Chanel. JOB COMPLETE | Nuisance Calls | Nuisance Calls | 0.99806
de-iced 2 evaporator coils, had Tech Support to put it through defrost and check parameters everything is operational | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9982
8/22/2023 10:36:21 PM Oleary, Holden -0001 Arrived on site and checked in with manager Nick. Case is low temping for LT-SC SD FF2a. Could not find case on sales floor or any where in the store. Spoke with manager and no manager or supervisor in the store knew anything about this case. Got with Novar and Walmart building controls and they had no info on location of the case. Manager said they have had this happen before and to return to speak with other manager at another time to locate case. Updated manager call in progress 8/23/2023 3:21:11 PM Oleary, Holden -0002 Arrived on site checked in with manager Got back with novar and continued to try and locate the low temping case ID LT-SC SD FF2a. Still cannot locate the case after speaking with store manager and novar. Found the blueprints for the store and was not able to locate via prints. Main store manager is not available to answer phone due to traveling. Continued to look for case and go through controller and went onto roof checking all self contains for issues. Case is not able to be located. Spoke with service manager and field supervisor both are in agreement this call will be closed out. Did last check in the curbside and cafe areas and case is not to found. Updated manager call is complete | Nuisance Calls | Nuisance Calls | 0.996
10/04/23 -Arrived on site and checked in with MOD and into service channel. -Accessed motor room and found rack holding suction psi. -Checked comp B3 and found compressor had already be replaced by cool sys. -Noticed contactor still needed to be replaced. -Turned off power to the rack and changed out contactor and auxiliary. -Restored power to rack and slowing cycled compressors back on. -Noticed pressure switches still needed to replaced also. -Will return compressor to United in Buena Park. -F/u to replace pressure switches once parts are available. -Job incomplete. | Compressors/Motors | Compressors/Motors | 0.99862
230719-0255 ST15:30-16:00 OT:16:00-00:00 8/5/23 OT:00:00-00:45 OT TT:00:45-2:15 arrived checked in With MOD gained access to Rack A, M&S picture attached valved off compressor #6 dumped remaining gas into suction header, removed compressor Installed new compressor. pulled vaccum to -30hg and performed decay test. leak checked compressor with bubbles and stratus, no leaks at this time. Opened valves back up fully and started compressor checked all safety’s and amp draws on start up. Everything running properly at this time. will follow up and recheck for leaks next week when I return to do compressor #5. pulled two gallons of POE oil off of truck 8036 (Jim) and input into compressor. Job complete. Checked out with manager. Just realized I’m on the wrong ticket compressor #6 was replaced on this ticket not compressor 5 we will be replacing compressor #5 next week on 230207-0113. | Compressors/Motors | Compressors/Motors | 0.9983
The manager was asked and alarms were verified and everything working was identified. the manager has no idea about this call. | Nuisance Calls | Nuisance Calls | 0.99822
7/20/2023 12:30:41 PM Smith, Stephen -0001 Time In: 20:30 Time Out: 20:45 All cafe coolers & freezers have been down for over a week. Main breaker panel for the RCU’s lost power at the transformer. An electrician was on site to fix the issue last week, but the issue came back the next day. Confirmed breaker panel is still missing L1 & L2. Electrician company has been called out by MOD to make repairs. Job Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99624
Arrived to job located rack b. Turned power off to compressor one replaced current transformer. Powered compressor back on. Called Sams support had them force compressor one on. Compressor operating and showing current on novar now. | Compressors/Motors | Compressors/Motors | 0.99855
Checked in with Charletta Let her know I will be checking the POS cooler for leaks. Headed towards the POS cooler and saw the light flashing outside of the cooler. Walked inside the cooler and found the Emerson leak detector to be at 0ppm. Grabbed my leak detector and started to walk around inside the cooler and found no leaks, my detector stayed at 0ppm. Removed the Emerson leak detector and did a power cycle on it to reset it. Once it came back on it was still reading 0ppm. I zeroed out the leak detector as well and still was at 0ppm. Called Sam’s technical support to see if they were able to see any refrigerant readings on their end. The tech checked all of the parameters for this case and everything was running good. The tech said they couldn’t see anything for refrigerant leaks on their end so they said they will have Novar give me a call to see if they can check more in depth. While I was waiting for a call back I started to leak check every unit on the sales floor to see if I picked up any leaks and I didn’t find any. After 40 minutes Novar called me back. I explained what was going on and they said they would check everything on their end. They put me on hold while they checked it out. Novar told me there were no alarms for leaks and they had me power cycle the leak detector system. That turned off the light that was flashing. Checked out with Jeff and let him know what was going on. Told him I called Sam’s technical support as well as Novar and they confirmed there were no alarms for refrigerant leaks. Kysor panel systems Serial: 21672011 | Nuisance Calls | Nuisance Calls | 0.99825
7/15/2023 4:54:08 PM Warden, Cody -0001 Checked in with manager/ Daniel Responding to A/c unit not cooling at fuel station. Lennox M/N XC13 -018 -230 -01 SIN 5807C21774 Checked thermostat and verified it was calling and working properly. Found condenser fan not running. Checked breakers to ensure they weren’t tripped and checked pressures. Pressures were good. Inspected condenser coils and found them severely plugged Cleaned coils with pressure washer and coil cleaner. Hit high pressure switch on condenser unit and unit came on and started cooling Checked out with mod/ Daniel Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99612
Sams club 4822 Wo#230720-0344 Po#251410835 Rack A -upon arrival to the store and I introduced myself with manager -call home office and asked at time it was created this call and they mentioned at 14:30pm and this call was dispatch at 19:00pm -over the phone we confirmed Rack A it is operating good with no alarms, having a 15psi suction and 225psi on discharge -job completed | Nuisance Calls | Nuisance Calls | 0.9981
We received the wrong compressor for this call. We took compressor back and ordered the new compressor. New compressor is six weeks out. Will return to install when new compressor comes in. | Compressors/Motors | Compressors/Motors | 0.99858
Found compressor locked out on oil. I reset compressor. Compressor is running properly | Compressors/Motors | Compressors/Motors | 0.99841
7/20/2023 1:48:06 PM Barker, Kenneth -0001 Both lights work tried on another case.Something’s wrong inside case and needs to be looked at by a refrigeration tech I have no way to check a ballast 9/14/2023 9:15:39 PM Sovran, David -0002 Arrived on site and checked in with manager mark. Mark directed me to the POs cooler and explained the lights have been out for the last week. Checked light switches to verify that lights weren’t turned off. Switches worked and went to look for ballast on the case. Wasn’t able to find it inside the case. Found junction box for the doors and lights. Opened up junction box and testing for voltage. No volts we’re coming from any of the circuits. Had a manager unlock the rack house and the electrical room. Began searching for the breakers for the circuit. Checked the electrical room looked for the breakers for the case. Went back to the rack house and began looking for breakers to the case. Found the breakers for the cooler door lights and began looking for a tripped breaker. No breakers were tripped. Went back inside and needed a scissor lift to get access to the top of the case. A second tech was called for safety. Once second tech came, brought second tech out to the floor to escort scissor lift to the top of the cooler. Once on top of the cooler. Began looking for ballast. Ballast couldn’t be found. Checked for voltage on top of the cooler. Opened up the junction box. Inspected wires leading down to the junction box down below. Had voltage of 115v. Power leading to the junction box inside the cooler had 0 v. inside the cooler. The piping leading to the junction box was forcefully ripped from the junction box and bent mid way through the piping. Second tech helped identify breaker responsible for power to junction box. Turned off breaker. Cleaned up area and secured all covers for junction boxes. Put scissor lift back. Updated manager Noel and chism. Checked out with manager Noel. Pushing to outside contractor. 9/15/2023 3:54:42 AM Scheel, Jaymen -0003 Arrived on site and checked in with David. Started assisting with with the lights on the walk in cooler. Started walking around the store looking for a ballast for the lighting system. Unable to find one in the case near the doors. Got scissor lift out and checked the top of the cooler and unable to find anything up there as well. Walked around and found all electrical panels in multiple locations. No ballast found. Checked the rack house and no ballast found. Started tested the voltage for the lights and found 120 at the top of cooler junction box and at the junction box inside the cooler found no voltage. Electrician needed. Updated manager Noel. Cleaned up and checked out with Noel. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99684
This call is a duplicate of Customer po#251682749 | Nuisance Calls | Nuisance Calls | 0.99825
7/19/2023 11:20:13 AM SCHUPBACH, DUSTIN -0001 Found comp 1 for B rack off on a fault. The flood back is still gone from rack after adjusting txvs yesterday. I condemned compressor and valved off. I got compressor info and will get a new compressor ordered. Rack still at suction pressure setpoint. 11/21/2023 12:45:54 PM Jenson, Tyler -0006 Returned to store with parts, Replaced compressor B, Replacd Contactor, Replaced auxiliary switch, Pumped in 1 gallon of poe 68. Leak checked with bubbles. Let compressor run. 2nd Leak check electronic leak detector, No leaks found. Compressor running between 7 and 8 amps on each leg. Checked ops OK. Took old Compressor for core return | Compressors/Motors | Compressors/Motors | 0.99855
7/18/2023. Checked in found the unit A-03 Had to get lift ,shut system down pulled fan guards off and found plastic in side drain pan and inside of drain line. De iced and got all plastic out cleared drain line and reinstalled fan guards then turn system all on . Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99854
Was already on site. Spoke with manager. Monique was told case maintain temperature throughout day called home office verify temperature log use probe to verify correct temperature on case AS10 Case is maintaining setpoint all at normal at this time this call is complete. | Nuisance Calls | Nuisance Calls | 0.99837
10/16/2023 7:01:11 PM Newbrander, Ryan -0002 Sam’s club 6235 Compressor hangs out Picked up parts from local parts house. Arrived at store and checked in with manager. Had employee remove compressor from back of truck and bring over to motor room. Disconnected all power and safety’s from compressor. Removed suction and discharge lines from compressor. Disconnected compressor from bench. Removed and installed new compressor on bench. Wired in compressor. Installed new safety’s and wired them in. Connected suction and discharge lines. Ran vacuum on compressor. Opened up liquid line and suction line and oil line on compressor. Added 2 gallons of oil to compressor and rack. Removed and replaced contactor and auxiliary. Turned power on to compressor. Compressor is running properly. Leak checked compressor and found no leaks. Job complete 10/16/2023 7:02:07 PM Guerena, Mike -0001 Checked in with mgr at arrival. Went to motor room and proceeded with compressor replacement. We removed wiring from bad compressor along with oil regulator. We removed oil fail and pressure control. We detached compressor from mounting plates. We then removed compressor from bench. Next we installed the new compressor to the branch and secured in place with existing mounting bolts. We then wired in compressors and installed new oil regulator. We then installed new oil fail and pressure control. We ran vacuum on comp. We then started up comp and added oil. Comp now back online. There is no fork lift operator at this time. We will need to return in the morning to pick up comp and load on to the truck. FOLLOW IP REQUIRED | Compressors/Motors | Compressors/Motors | 0.99845
Arrived to store for all rack repairs. Replaced all parts that were ordered on quote and verified rack operation. While on site assisted in completion of rack B compressor swap. No further issues found at this time. | Compressors/Motors | Compressors/Motors | 0.99834
7/28/2023 3:18:10 PM Hanamornsate, Thirathanawat -0001 7/28/23 TH TT: 8:00-9:30 Time in: 9:30 Time out: 14:00 Refrigerator (Break Room) True MN: T-23-HC SN: 10529373 Checked in with Service channel and MOD. Checked the location. Found the iced up the Coil. Plugged out the power plug. Take the Fan plenum out. Used bucket contain hot water and Deiced Coil. Dry inside the refrigerator. Put the Fan plenum and Drain pan back. Plugged in the power plug. Door gasket is good. Checked the temperature. It’s showed 37 degrees F. Informed and checked out with MOD and Service channel Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
On site. Labor: 1415-1745 Travel from: 1745-1815 Began coating of the drain pans float. This time using a “high heat” coating rated for 1200°f. Made multiple applications about every 15minutes. Worked on Gro freezer A3 in between coatings. Fans not running, found a switch off. A02 and A03 freezer operating normally. Final coating made at 1700. Will come back tomorrow evening when float is tack free. Follow-up. | Nuisance Calls | Nuisance Calls | 0.99792
8-9-23 Paul Z / deice drain pans / coils System MTB WIC assisted Jose C -please see notes Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
Ti 1200 To 1345 1.75 Found that the wi cooler is off for the bakery. Called store support and had them suppress the alarms for 1 week to allow them time to finish the floor. And stop anymore automated work orders from being created for this walk in . Everything is working properly. | Nuisance Calls | Nuisance Calls | 0.99828
OT 2100-0000 TT/OT 0030-0100 Already on site for another wo While checking in with manager saw bs5 a-f warm Manager thought I was here for this call Called dispatch had call sent to me Closed BV let cases deice While deicing found bs5F coil 1 fan plenum not on correctly Bs5F coil 2 sensor bad R&R with 10k sensor Now reading correctly Bs5F coil 1 needs new fan assembly Found Bs5B coil 1 fan unplugged Bs5A coil 2 need new evap fan assembly BS5B coil 2needs new fan assembly I then tested every DA sensor Moved location of multiple sensors All sensors are now reading correctly Tested every coil out let sensor Every sensor is reading correctly Verified eepr is programmed for correct steps Both eev and eepr are programmed to 2500 steps Will verify steps from part # in am Will fu in am with parts Will also need to verify control pressure psi It’s set to 43psi converted is about 9 Will also need to submit program change Rs sheet calls for 4 defrosts a day There are currently 6 defrosts programmed I will fu in am | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99804
Checked in with Emilio Let him know there is a compressor that is off in rack A. let him know I need the rack house open so I can go in and check it out. Once I was at rack A I checked the oil pressure for the compressor and tried resetting them to see if it would turn on but it did not. Checked suction and discharge pressures and they were good. Checked the controller to make sure it was calling that compressor to turn on and it was. I removed the contactor cover to see if the contact points were okay. Noticed they were pitted and not in good condition. Contactor is bad, went to the parts store and got a new contactor and auxiliary. Arrived back on site and replaced contactor and compressor 5 is still not turning on. Checked voltage for all of the connections going to compressor 5 and everything was receiving power. I noticed on the board that compressor 5 output did not have anything hooked up to it. I checked voltage coming from that output and did not get any power coming out. I turned the switch from auto to on one by one to see what was controlling each switch. I found that output #10 when I turned it to the on position it would turn on compressor #5 I called Sam’s tech support so I could speak with Novar. They were not able to verify that output 10 on the board was controlling compressor 5 and they were not able to help me out. Everything is running as it should as of now and pressures are good. Checked out with Hamid Job complete Rack a R-422d Discharge psi 245 Suction psi 48 Reciever level 25 | Compressors/Motors | Compressors/Motors | 0.99852
8/10/2023 6:17:28 PM Sparks, Scott -0001 Checked in and out with candy Checked opes on cooler door. Found several doors needed adjusting. Adjusted all POS FREEZERS AND COOLER DOORS as needed. Checked all other doors in store. All ok. Meat door has been hit by forklift. Separate call was placed. Will follow up on Monday 8-14 per manager Ray. This call is completed. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99731
Checked in with manager Daniel, inspected the coils and saw that the drains were clogged and some of the screws were missing from the fan guards. The fan guard screw holes are on the drain pan so the missing screws were causing the water leak on top of the drain being clogged. I blew out the copper drain with compressed air and replaced the missing screws. Some of the holes were worn out already so I had to use different size screw to accommodate for the bigger hole and a bolt for one particular hole. If the holes get any bigger, they will need to be re-machined to get the holes back to normal size or get a new drain pan. Evaporator B9a MODEL # WK130AC SERIAL # D0F10457 EVAPORATOR B9b MODEL # WK130AC SERIAL # D04F10458 let the manager know that the leak is fixed. Checked out with manager Daniel Call Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99813
The 3 rooms upstairs (office, quiet room, meeting room) are too hot. Needs to be cooler. Checked in with Veronica/Kelly. Went upstairs and each room felt hot. Went up to roof to RTU 20. Suction at 155 psi and discharge at 323 psi. Verified compressor running, cfm running, and blower. Belt looks good. TXV feeding. Economizer closed. Found filters plugged. Removed. Checked other filters on units while walking back to roof hatch. Filters plugged. Was asked to check receiving office AC. Went to e2 to verify status for RTU 20. Went to RTU 13. Suction at 145 psi and discharge 319 psi. Verified compressor running, cfm running, and blower. Belt looks good. TXV feeding. Economizer closed. Found filters plugged. Removed. Went to each room. And each room felt cooler. Called home office informed Marugerite of issues. She changed setpoint to 72 for both. And verified “occupied” status for both RTUs. Informed Nicole and Christian to call filter company to replace all filters for each RTU. Job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99733
Travel: 0845 Time in: 1030 Time out: 1430 checked in with MOD Located produce walk in cooler Produce cooler has no roll down door Used ladder to access top of unit Took picture of serial number Sent information in to get roll down door ordered Spoke with manager about roll down door Chrscked iut with MOD F/U when part comes in to be | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99718
Andrew Debeaulieau 7/28/23 Travel 0600 Arrival 0700 Departure 1000 Found bakery cooler C08 high temp. Superheat is 57degrees; frost line between screen and body. Pumped down circuit and cleaned screen. Returned circuit to Norma operation. Coil split 10degrees with 13 degrees superheat now. Box temp pulling down. Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99828
Checked in with the Site Manager. I checked the MTC Open Case Cooler. The temp on C15C is currently at 25 Degrees F. I checked the Compressor Rack for this Unit and Everything is working OK. 8:00Am-8:45Am Travel 8:45Am-4:00Pm Labor 4:00Pm-4:30Pm OT Labor | Nuisance Calls | Nuisance Calls | 0.99798
8/13/2023 8:24:18 AM Dias, Kenneth -0001 Arrived at meat department removed panels water was about 2 inches deep in the case had to get some CO2 from United and clear out the drain Drain cleared and case cleaned Leak repaired | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
Anthony Robak Checked in with MOD Went to front of club pickup for LT-SCa Found case at 1 degree even with door open Case has good airflow Due to high traffic this case struggles to get down to setpoint Management aware Case at 0 degrees at time of departure complete | Nuisance Calls | Nuisance Calls | 0.99807
Start time-1130 End time-1245 complete check in with manager Jay Perez cafe exhaust is working lights on the exhaust assembly is not working put a new bulb in socket still didn’t work, switch getting power, no power going to the lightbulb socket advise manager jay perez to get an electrician out to have a look at it checked out with manager jay perez | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.9969
8/8/23 Arrived onsite and checked in with the manager (Mario) I found this case not refrigerating So I went thru and checked fans The coil to see if it was iced over All looked good So I went to the Rackroom and checked compressors any alarms I checked the circuit and I found that the liquid line ball valve was closed I open the valve and checked the case I let it temp out and told Mario the case is good to go They have construction going on here so they might have turned it off by accident THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99827
7/27/2023 7:28:31 AM Buenrostro, Juan -0001 Arrived to store located fan making noise found that wire was hitting fan blade causing noise. Had to remove fan to repair wire. Was able to install fan back and keep wire away from fan blade. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99706
Jansen Pulido 11-7-23 Travel 0530 Arrive 0800 Depart 1345 Travel 1430 Checkin Taola Arrived and checked in with TOS, Jake Dicecco RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call compete. | Capital Replacement | Capital Replacement | 0.63498
Checked in with manager Wo order placed so they could order curtain. Closing out ticket per manager. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99581
Unit: Rack Back -upon arrival rack B opus com loop was not communicating. -searched the entire circuit then found the issue at case BS07. After giving the S3C a power cycle all the cases came back online. -no other issues system operational. | Nuisance Calls | Nuisance Calls | 0.99799
07:45 am -1100am (3.25 AFH) Arrived on site with primary tech James. Checked in with MOD. Walked into bakery and inspected freezer door. The door isnt sealed correctly because it looks like it was hit with forklift. We tried to adjust the door, but the weight of it wont let it sit right. Will have to return with brackets and cement drill to fix issue. | Damage by Customer | Damage by Customer | 0.98714
8/4/2023 6:42:00 PM DeBeaulieau, Andrew -0001 Kysor-Warren OIV5V14-03UN 0809001758 Found txv has high superheat cause inefficiency in cooling. Pumped down system and cleaned txv screen. Return case to service. Call complete 8/8/2023 5:59:27 PM DeBeaulieau, Andrew -0002 Confirmed case is below 0 degrees. Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99805
Completed Arrived on site, Picked up uhual needed to remove old door and crate. adjusted door electrical wiring for heater, adjusted door height and door handle to appropriate levels to ensure seal. Returned to trashed out back, loaded up uhual with old door, and it’s crate. Returned to shop to trash items. Recycled door. Return rented uhual trailer. Returned to Sam’s to check out. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99685
Time in: 1045 Time Out: 1330 CS10a Service Meat Case High Temp (Home Office Call) Hussmann (CS10a) M# Q3-M/FV-EP-8-R S# 971936 Located CS10a case. Case temp reading 56 at Novar controller and confirmed at case thermometer. Staff still had product in the case. Asked staff to move product. Removed deck pans to access the coil, and the coil had a large amount of thick frost build up(not so much solid ice). Closed off the hand valves to each coil, and de-iced entire case with hot water. Let the coils dry off for about 20 minutes and then opened the hand valves back up. Case temp dropped down to 26 after about 10 minutes. LT-SC1 IC DRS high temping (Home Office Alarm) Hussmann (CPU Freezer) M# RFLN3 S# MY18E041362 R-448a Located curbside pick-up freezer case temp reading 9 on arrival, but staff said that it’s high because of high traffic and the freezer is right next to the exit door. I cleaned the condenser coil, it was caked with dust. Suction pressure @ 24 psi, sight glass solid column, entire case has strong airflow and the coil is not iced up. Monitored the case for awhile and watched it hit sub-zero temps. Jobs Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
8/25/2023 5:02:57 PM Del Rio, Gabriel -0001 Arrived on site checked in with store manager MT8 walk-in dairy box door has damage to it door was damaged from remolding construction crew who installed it manger said that he’s going to find out if the initial installed company is going to re install new door call complete | Damage by Customer | Damage by Customer | 0.98503
Replaced bottom guide rail for sliding POS freezer door. Door is now staying in the track. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99694
8/21/2023 6:06:55 PM Calderon, Jose -0001 Checked in with manager Ellen, checked the unit and the board was frozen, I reset the unit by power cycling the RTU and the unit started up on its own. I called Novar to confirm temps and they said it was set to 73F and currently the unit was at 73F. History showed someone had changed it to 68F some months ago and then it was changed back by corporate. I checked pressures to ensure it wasn’t low on refrigerant. I checked the fan operation and it is running, I checked blower and it was running normally. I checked temp sensors and they are running normally. Unit is running properly and there is no alarm present for this unit. I let the optical associate know that if they want it changed permanently they need to have their manager submit a change request form to set it. Other than that, the unit is running and operating properly and at target setpoint. Confirmation by Novar. LENNOX RTU 23 MODEL # LGE060H4BH20 SERIAL # 5604E03211 Let the managers know the unit was running properly. Checked out with manager Antonio Call Complete 8/28/2023 11:02:42 AM Calderon, Jose -0002 Checked in with manager Cheryl, this is not a recall, the manager marked this call unsatisfactory because there was confusion about how this was to be resolved. They wanted to lower the temp set-point in the room and needed to have corporate change the set-point. I was able to change the set-point last time but only by a few degrees. So they need to contact corporate to make bigger changes to the set-point. I called building support and had them confirm the RTU is at a set-point of 71F and it is currently at 71F. I had them annotate it in the work order as well. LENNOX RTU 23 MODEL # LGE060H4BH20 SERIAL # 5604E03211 I spoke to the manager and let them know that the RTU is working properly and that they need to have corporate make the change to the set-point if they want it colder but right now it is set to 71F and is currently at 71F. Checked out with manager Cheryl Call Complete | Nuisance Calls | Nuisance Calls | 0.99805
7/20/23 MTB RCU3 -Arrived on site and checked in to service channel and in with MOD. -Located dairy coolers temping warm and didn’t find anything wrong with evaporators. -Gained roof access and located condenser associated with RCU3. -Found compressor offline with no power to unit. -Traced power back to electrical panel and found breaker for RCU3 tripped. -Tested compressor terminals to ground to verify compressor was not ground. Compressor ok, not ground. -Checked windings at compressor and got continuity. -Tightened all electrical connections and verified no burned wires. -Reset breaker to RCU and monitored system ops. -Case temp dropped and compressor and condenser fans working properly at this time. -Suspect breaker may be going bad and will need to be replaced. -All system ops ok at this time. -Job complete. | Compressors/Motors | Compressors/Motors | 0.99852
TTST 1200-1230 Time in 1230 Time out 1800 Rack C M# PS S# 107351 Tg# 0028297 Rack was pumped down at CDS valve coming off subcooler providing liquid for liquid header. The Novar subcooler board was not working. Checked wires, found power wire loose on board. Tightened power wire on board and board started up, CDS valve opened and rack started up. Temperatures all dropped. Monitored operation. Helped Jim out with rack B. Checked out with manager Jamaily. Complete | Compressors/Motors | Compressors/Motors | 0.99837
On-site 1645-1815 Sys MTB-s4f On site. Checked in service channel. Found floor sink for island m/d cases plugged and overflowing. Removed guard rails and toe kicks. Screen for sink was plugged full of slime. Dumped and cleaned out in mop room. Cleared floor sink with co2 and rinsed with buckets of hot water. Mopped up as much water as I could. Put back toe kicks and rails. Checked and found other floor sink on the island plugged up as well. Cleaned and rinsed with buckets of hot water. Cleaned up water from floor. Informed manager of findings and that there is still a small amount of water under cases that will need to dry. Job is complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99822
8/1/2023 5:29:40 PM Garreans, David -0001 Time in 1830 Time out 1845 Checked in with manager Oscar. MTBS14a M# OM8NRG S# 1099146 Tg# 0035447 BS05a M# OM12NRG S# 1098626 Tg# 0035472 This was a duplicate ticket , took care of issue on first ticket for this. Checked temperatures of each case. All are not in alarm. Complete | Nuisance Calls | Nuisance Calls | 0.99831
TT:7:30-8:30 ST:8:30-13:00 with lunch Arrived checked in with manager Rudy Gained access to the motor room Located Rack A, noticed that the liquid level was at 15%. Graphed it out and has decreased slowly overtime. Added 48lbs of 404a to bring system back to 30% Leak checked condenser, Rack B and all cases associated to Rack B, found leak at the compressor #2 discharge king valve that has been valved off due to bad compressor, tightened valve and used nylog and installed cap back leak is repaired for now valve will need to be replace when compressor is changed to avoid any leaks in future. Also found leak at the bottom of oil pump housing tightened the bolts and rechecked as well leak is repaired Rechecked with leak detector and bubbles. No other leaks found at this time. Ran leak detector over rack b again to insure no other leaks at this time and nothing picked up. Advised team that when compressor is replace that the valve will need replaced as well due to blow by. Checked out with manager Rudy. | Compressors/Motors | Compressors/Motors | 0.99796
TT 1100 check in 1230 checkout 1530 Check with manager at the arrival and check RIIC case sys A5b found case with not air flow, evaporator coil was iced up I asked manager to remove product to deiced evaporator coil, deiced evaporator and check heaters , defrost system is working properly, no more problems found | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
Incomplete Arrived on site and checked in with the manager. Went to the roof and found the unit was off. Unit not showing up on the controller. Had to set the unit to run in stand alone mode at the controller. Assisted the other tech with other calls while onsite. | Nuisance Calls | Nuisance Calls | 0.99825
LTA-2/3 Walk In Freezer Door Time in 0830 Time out 1700 7/31/2023 Robert F & Dylan L Upon arrival checked into ivr and with mod. Accessed first walk in freezer and found door rubbing on floor and jamb gaskets on sides damaged. Also stay rollers not in proper position for door to close and seal properly. Found door on handle side with metal coming apart and catching on gaskets. Removed damaged jamb gaskets and raised door up to stop rubbing on floor. Repaired door metal damage and installed new side jamb gaskets with pointer screws. Then adjusted stay roller on left side of door. Then had to move stay roller on handle side to a better position (used one concrete anchor). Then adjusted stay roller for proper closing. Then added a guide spacer to prevent door from hitting left side jamb gaskets every time door is opened or closed. Cleaned work area job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99721
7/26/2023 Bob On arrival tech check in with service channel and store manager. After picking up parts. Removed all damaged door gaskets and installed new magnetic door gasket on both 3 door merchandise cases in front entrance. Adjusted 1 door to close properly. Job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9973
Start time-1145 End time-1400 complete check in with manager Oscar 3 glass door not shutting all the way due to master rod loose and rubber gasket not full on tighten master rod on one glass door and took gaskets off off all 3 and readjusted them checked out with manager | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99729
Assitedbin the repair of rack C opened up extra discharge line replaced discharge control on comp 2 all ok | Compressors/Motors | Compressors/Motors | 0.99835
8/14/23 TH Time in: 16:00 Time out: 19:15 LT-CU2: Cafe FZR Heatcraft MN: LET065BEK SN: T12A15382 Arrived on site and checked in with Service channel and MOD(John). Found Evap Coil iced up and box running 28 Degrees F because the strip curtains were opened and slide to both sides. Turned off the Breaker. Ran the water hoses. Take all Fan guards and Fan blades out. De iced the Coil. Put Fan blades and Fan guards back. Found drain pipe (PVC section) was broken. Went to Home Depot for pickup parts. Went back to the store. Removed bad Drain pipe out and installed new Drain pipe in place. Water test and no leak. Turned the breaker on. Called defrost and heater are working good. Called refrigeration mode and checked the temperature showed 11 degrees F. Needed to be close the Door longer but the Employees needed to be open for pickup product inside. Cleaned work area. Informed and checked out with MOD(Lakisa) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
7/25/2023 JH TT 0730-0830 ST 0830-1030 -upon arrival checked in with store manager -shown drain pipe dismounted from wall -picked up parts from parts house -returned to store -remounted drain pipe into wall -checked out with store manager | Damage by Customer | Damage by Customer | 0.95895
Time in 1730 Time out 1830 Quote to clean coils Log into service channel and check in with manager for dairy WIC leaking water -found case at temp -inspected coils -coils have heavy debris and need to be cleaned -quote to clean coils 2 techs 8 hours each | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99799
Jul 21, 2023 Found VFD in bypass. Checked all fans, all fans operational. Reset VFD, 105° ambient temp. Condenser tripped again, creating high discharge pressure. Condenser tripped again on earth fault #2. Checked motor winding, good. Checked motor shorts to ground, none found. Found rub out on wires going to motor, cut shorted wires out and reconnected. Condenser now out of bypass. Now at 307 psi, down from 320. Compressor is on order on other work orders. No temp issues. | Compressors/Motors | Compressors/Motors | 0.99853
7/19/2023 7:45:32 PM Stuart, Christopher -0001 En Route: 1230 Time In: 1345 Time Out: 2045 LTA a01/a02 High Temping Checked into Service Channel Checked in w/MOD Veronica Located LTA A01/A02 freezer. The freezer door was already condemned and pending replacement. The door is intermittently operational, but someone disengaged the motor brake, and the door was stuck open. Re-engaged the motor brake, reset the door open/close parameters and the door is operational. Per case temp sensors, temps ranging between 5-15. Coils are not iced. Rack suction pressure swinging between 15-18 psi. Comps 3-5 were not online. Found compressor toggle switches had been replaced, but they were toggled off. Found fuses for control voltage were blown. Replaced fuses and compressor’s came back online. Suction pressure dropped to 13 psi. POS box temp also started dropping closer to set point. Condenser coil was clean and all fans operational. Checked out w/MOD Javin Checked out of Service Channel Job Complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99644
Arrived on site went to back found manager JT and asked about line he said its been leaking smelled like gas line they valved off the heaters I stated to manager if the gas line is leaking it would be the plumber not us and he stated then why was I there if I couldn’t fix it stated to customer they put HVAC as the source customer got angry grabbed my things as we the technicians are there to try to fix the issues not get yelled at by customer when they couldn’t put the wo in correctly | Damage by Customer | Damage by Customer | 0.97401
Check in with mod check compressor rack A found compressor off on oil clean oil strainer and turn compressor back on check for properly operation need follow up 8/28/2023 Monreal, Jesus -0001 Gp# 230819-0001 Check in with mod Check alarm on compressor rack A follow up on the alarm check compressors for properly operation no more alarms compressor rack working properly all temperatures at set point complete 8/29/2023 Monreal, Jesus -0002 8/28/2023 Monreal, Jesus -0001 Gp# 230819-0001 Jesús Monreal 08/28/23 Check in with mod Check alarm on compressor rack A follow up on the alarm check compressors for properly operation no more alarms compressor rack working properly all temperatures at set point complete | Compressors/Motors | Compressors/Motors | 0.99862
Main cooler Freon alarm is going off Please provide club managers c 7/28/2023 6:28:09 PM Gonzalez, Alan -0001 Checked in with Charletta Let her know I will be checking the POS cooler for leaks. Headed towards the POS cooler and saw the light flashing outside of the cooler. Walked inside the cooler and found the Emerson leak detector to be at 0ppm. Grabbed my leak detector and started to walk around inside the cooler and found no leaks, my detector stayed at 0ppm. Removed the Emerson leak detector and did a power cycle on it to reset it. Once it came back on it was still reading 0ppm. I zeroed out the leak detector as well and still was at 0ppm. Called Sam’s technical support to see if they were able to see any refrigerant readings on their end. The tech checked all of the parameters for this case and everything was running good. The tech said they couldn’t see anything for refrigerant leaks on their end so they said they will have Novar give me a call to see if they can check more in depth. While I was waiting for a call back I started to leak check every unit on the sales floor to see if I picked up any leaks and I didn’t find any. After 40 minutes Novar called me back. I explained what was going on and they said they would check everything on their end. They put me on hold while they checked it out. Novar told me there were no alarms for leaks and they had me power cycle the leak detector system. That turned off the light that was flashing. Checked out with Jeff and let him know what was going on. Told him I called Sam’s technical support as well as Novar and they confirmed there were no alarms for refrigerant leaks. Kysor panel systems Serial: 21672011 | Nuisance Calls | Nuisance Calls | 0.998
8/10/2023 3:06:13 PM Hanamornsate, Thirathanawat -0001 8/10/23 TH TT: 13:30-13:45 Time in: 13:45 Time out: 17:00 RCU-1 Heatcraft MN: LLE170BEK SN: T17H00018 Arrived on site and Checked in with Service channel and MOD (Lesley). Checked the location. Found the Main drain pipe had gunks inside the pipe. Found Coil and Drain pan were dirty. Ran the water hoses. Turned off the unit. Cleaned the Coil. Dropped the drain pan down and cleaned it. Flushing drain pipe by CO2. Put it back. Turned the unit back on. Put a gallon of the water for test and no more leak water. Flushing main drain pipe by CO2 and checked it. No more gunks inside the pipe. Cleaned work area. Informed and checked out with MOD (Laura) and Service channel. Job finished 8/10/2023 3:43:46 PM Smith, Stephen -0002 Time in: 13:45 Time Out: 16:45 Assisted lead tech lit clean coil and unclog drain lines and clean cafe walk in cooler. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99825
8/15/2023 8:44:50 PM Young, Robert -0001 Arrived on site and checked in with the manager. Went to the roof and started to going through the RTU’s and AHU’s and the units we couldn’t get on network. Put them on stand alone to get them cooling. AHU has a short that has to be located and RTU 13 control board screen is blank. Will have to order a control board for 13. 9/19/2023 3:52:06 PM Young, Robert -0002 Arrived on site and checked in with the manager. Went to the roof and found the unit is running and back online. Had to address unit 20 and 16 to keep the network from going down. Break room unit 21 is working properly and at temperature. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99569
8/7/2023 Bob E and Glenn Sr and Robert On arrival tech check in with service channel and store manager. Had to cut off bent concrete anchors then lift inside walk in cooler safety poles and move out of way. Found a lot of concrete damage. Cleaned up all broken and cracked up concrete. Filled and leveled concrete with concrete epoxy. Set safety poles in proper position and installed new 5/8x6” concrete anchors with floor shims to make poles plumb.Also repaired top U bolts and tighten down and secures top safety pole cross member. Cleaned up all area job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99654
On-site 2230-2400 Arrive on site. Checked in with manager, Chapra Model: 03.5UM6 Made way to grab and go case for cafe, MTCU1 Removed drinks from cooler Removed panels to access evap coil Found evap coil iced up Also noticed water leak on floor around cooler Main drain line is clogged, informed manager that plumber needs to come out and fix the drain. Manager requested that we come back to diagnose as they are closing the store for the night. Incomplete follow up Returned 8/14 Arrived on site. Checked in with Shaik. Condensing unit model: BHT015X60 serial: T10B05108 Made way to rcu1. Cycled power on Evap coil is thawed out All fans are running Noticed manual valve was not open all the way Open valve completely Suction pressure @ 71psi Cooler temp is down to 36° Tested defrost cycle and ensured proper operation Cooler is operating properly Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
Completed Checked in with manger on site went to roof top for grab and go case unit found it wasnt running so inspected everything found it had a bad contactor so replaced contactor with a new one everything came on as it should an started dropping temp no other issue found. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99655
TTST 0830-1000 Time in 1000 Time out 1815 Checked in with manager Alberto. Rack C breaker had tripped due to bad compressor 3. Tech Lit will turn in information for a quote to replace on his ticket that he is on. Compressors were not staging correctly. Was on phone all day with Novar getting staging corrected and they put in an override off on compressor 3 so it will not try calling for it on staging. When compressor gets changed Novar will have to put back into staging. Suction pressure came down and all temperatures on rack C dropped out of alarm. Checked out with manager Marcus. Complete | Compressors/Motors | Compressors/Motors | 0.99856
8/3/2023 2:22:32 PM Hernandez, Cynthia -0002 MT2 grab n go case by cafe leaking water. Hussmann ID5SM6 MY19E038929 On site already. Asked to get product pulled from bottom shelf. Found case drain clogged. Cleared with co2. Found water stuck underneath both plenums. Closed off hand valve and unplugged fans. Cleaned case with hot water and remove all slime and trash from case. Cleared with co2 again. Put case back together. Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
8/2/2023 8:01:10 PM Calderon, Jose -0001 Checked in with manager Daniel, inspected the coils and saw that the drains were clogged and some of the screws were missing from the fan guards. The fan guard screw holes are on the drain pan so the missing screws were causing the water leak on top of the drain being clogged. I blew out the copper drain with compressed air and replaced the missing screws. Some of the holes were worn out already so I had to use different size screw to accommodate for the bigger hole and a bolt for one particular hole. If the holes get any bigger, they will need to be re-machined to get the holes back to normal size or get a new drain pan. Evaporator B9a MODEL # WK130AC SERIAL # D0F10457 EVAPORATOR B9b MODEL # WK130AC SERIAL # D04F10458 let the manager know that the leak is fixed. Checked out with manager Daniel Call Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99783
Andrew Debeaulieau 8/8/23 Arrival 1600 Departure 1645 Confirmed case is below 0 degrees. Call complete | Nuisance Calls | Nuisance Calls | 0.99823
Favian Porrata 07-25-23 Travel 1000 Arrival 1100 Departure 1345 RTU 15 Lenox M#SCA240H4MN1G S#5608G14113 Upon arrival checked in with Manager Peter. Call was for RTU 15 not on. Began by checking if the disconnect was off and it was. Started to do my inspection of the unit. Made sure compressor where good. Than began to check belt and inspected blower wheel. Checked to see if the filters where good and they are. Made sure to check wiring for anything that looked out the ordinary. Everything checked out turned unit back on. Unit is now running and has a 23 degree split. Call complete. | Nuisance Calls | Nuisance Calls | 0.99824
Arrived to job checked in with manager. Manager showed me location cooler making noise. Found coil b04 and b03 iced up and drain clogged. Washed all ice from coil and cleared drain line with co2. Cooler operating proper at the time. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
8/19/2023 3:47:46 AM LONCASTY, SEAN -0001 Found two comps off on high head pressure,reset. | Compressors/Motors | Compressors/Motors | 0.99836
Travel: 0630-0830 On-site: 0830-1400 On arrival checked in with store manager and directed me to produce walk in cooler and stated one of the fans were not working. We waited for customers to finish there shopping at produce cooler. Once clear i had an employee spot to get scissor lift from receiving to produce cooler. Found that evap motor was in good condition of fan blade was damaged. Went to local supply house and picked up anew fan blade and made replacement. Installed and verified normal operation. Notified manager about findings and CALL IS COMPLETE | Compressors/Motors | Compressors/Motors | 0.99538
8/7/2023 7:31:29 AM Floyd, Kaden -0001 Arrived on site to work on bunker case leaking water I checked in with manager to let them know what I was doing then I went to the case and pulled the bottom of the case to access the drain and I had them pull a section of the case so I can get to the drain pan once they moved it all I removed the shelves and the fan motor and saw the drain pain had been rusting out and is leaking thru little holes so I talked to the manager and ask if they wanted to shut it off for a day and let it dry out so we can seal the pan but they said the remodel gets started on the store in a month so don’t worry about the pan | Damage by Customer | Damage by Customer | 0.98085
Produce MTC-1 Walk in door 07/16/2023 Dylan Lopez Travel time 09:00 Time in 10:45 Time out 12:15 Arrived on site checked in and out with manager and service channel went to MTC-1 found door not lined right. Verified with store manager Robert that 2 techs will here at 20:00pm Tuesday night to fix door verified with bob emmer that it’s a non mech issue pics on mobile tec verified with supervisor call incomplete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99609
8/2/2023 5:35:08 AM Hanamornsate, Thirathanawat -0001 8/1/23 TH Time in: 17:00 Time out: 20:00 C11a: Produce CLR Heatcraft MN: WKE340BEC SN: T17D13991 C12a: Heatcraft MN: WKE340BEC SN: T17D13993 Arrived on site and checked in with Service channel and MOD (Josh). Checked the location and Found water condensate started dripping to the floor from both units. Found both Coils were very dirty. Turned off the Fan switch and take all Fan Guards and all Fan blades out and cleaned them. Cleaned the coils by brush and keep all dirt out from the drain pans. Put all Fan blades and all Fan Guards back. Cleaned drain pan by water and flushed drain pipes by CO2. No more water dripping. Cleaned work area. Informed and checked out with MOD(Josh) and Service channel. Job Finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99856
8/10/2023 7:18:16 PM Alcaraz, Jose -0001 Time in 1730 Time out 1800 On site got a call for LTB comp 5 -found compressor not running -checked operations -found compressor bypassing -need to quote out compressor 9/29/2023 11:40:47 PM Maldonado, Chris -0002 Start time-0700 End time-1800 check in with manager Matthew queen found compressor MTB #5 in back receiving, called united to verified that we have the right compressor verified compressor had no power closed all valves to compressor verified no pressure left in compressor drain all oil from compressor unwired, unbolt compressor took old compressor off b rack and put new compressor in wired and bolt new compressor, leak check wired in new DP340240F DEFINITE PURPOSE CONTACTOR 3 POLE 40 FLA 240 VAC COIL, Auxiliary Switch 1950243 pulled vacuum, open system, leak checked once more turned on the breaker compressor did not turn on. called home office to verify that the compressor is on (yes) follow up for high level teach check out with manager Matthew queen 10/1/2023 8:27:40 PM Toomer, Collin -0003 TT:6:30-11:45 ST:11:45-14:30 with lunch OT:14:30-18:00 OT TT:18:00-21:15 Arrived checked in with Mathew Gained access to the motor room. Assisted lead tech with compressor change on Rack B. Compressor #5. M:PS S/N:59210-3 After installed compressor we leak checked and started compressor. The compressor isn’t coming on called David and ran some test. Chris M. Called Jonathan and he advised put in for follow up and they will return next week. Call incomplete Needs follow up Checked out with Mathew. | Compressors/Motors | Compressors/Motors | 0.99855
Return to site logged in with service channel access roof hatch located photo cell. Verified power checked comm wires. Tested photo cell did overview on novar controller for any alarms present. Visually inspected for any damages or burned components. Did not find any issues light operating properly. Arrived on site logged into service channel spoke to Crystal W. access electrical room inspected electrical components. Did an overview on novar controller verified dials. Could not access roof hatch will have to return to continue diagnosing. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99733
TT/OT 1800-1900 OT 1900-2100 Arrived on site checked in with service channel and manager Found fan unplugged Sys bs07 Plugged fan in now at temps Sys B4.1 found honeycomb Blocking air flow Installed honey combs correctly case at temp Verified opus controller is able to see case Please see pictures call complete | Nuisance Calls | Nuisance Calls | 0.99822
8/1/2023 5:57:34 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke with the manager, Christine. I looked over the rack and found compressors were working and temperatures are coming down. I was advised that someone had already restarted the compressors because they were off from the plumbing work that was being done on the cooling tower. I spoke to Christine and told her what I did and what I found. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99816
7/19/2023 8:06:23 PM Biggs, Aaron -0001 TRAVEL TIME=0700-0800 TIME IN=0800 TIME OUT=0830 07/19/23-AARON BIGGS-SYSTEM#C7-b PREPED MEALS CASE UPON ARRIVAL CHECKED IN WITH MOD JAIME. Call is duplicate call. Confirmed call is a duplicate. REFER WO#230719-0085 PO#251289427 JOB COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99832
7-21-23 ID Call for warm air over produce Checked in with manager Located RTU above produce, RTU 3 Gained roof access, located unit on roof and found in idle mode, located controller and found not calling for cooling, zone at temp Called home office and verified setpoints correct, verified system set for occupied space settings, located sensor and verified reading properly, sensor not mounted correctly secured sensor, verified economized closed and not blowing outside air in, tested cooling at unit and verified working properly Notified manager Job complete | Nuisance Calls | Nuisance Calls | 0.9984
Measured air curtain and will have replacement ordered | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99594
9/12/2023 9:58:24 AM Manaog, Efren -0001 Arrive onsite and checked in with service channel but the tracking number is closed. Checked in with MOD Serked A05 & A06 -Checked the circuit and it is cooling properly. A05 just got out of defrost and temperature is coming down close to the set point. Checked all the product and they are frozen -Went to the rack house and no issue found. No alarm for these circuits. Sight glass clear and receiver level at 35% -Searched history. Repair is complete. Refer to WO 230824-0210 -Locate manager and talked to MOD Serked and explained what I did -Job complete | Nuisance Calls | Nuisance Calls | 0.99834
8/23/23 RM St 1430-1900 Assisted lead technician on compressor change out | Compressors/Motors | Compressors/Motors | 0.99856
7/25/2023 3:08:50 AM Biggs, Aaron -0001 TRAVEL TIME=0 TIME IN=0400 TIME OUT=0415 07/24/23-AARON BIGGS DUPLICATE CALL. PLEASE REFER TO WO#230717-0357 PO#251131478 JOB COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99825
Arrived to job located racks on side of building. Accessed rack b comp 1 staging on and off as it should still showing alarm. Need to order a new current transformer. Will return to install. | Compressors/Motors | Compressors/Motors | 0.99847
7/24/2023 8:18:40 AM Maldonado, Chris -0001 complete checked in with manager checked case for temp. (Running at temp 31) checked history was complete on 07-22 checked out with manager | Nuisance Calls | Nuisance Calls | 0.99837
Completed. Checked in with management. Moved pallets in freezer. Accessed evaporator with scissor lift. Removed temporary transformer and installed the proper one. Waited for escort for the scissor lift. Function tested equipment. No further issues. Waited for proper temperatures to be reached. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99594
Jul 17, 2023 Found compressor off. Reset OPC, compressor came back on. Checked net oil 40 psi, found high discharge pressure 285. Found 2 CFM not spinning, checked windings and both motors ok. Checked shorts to ground, none found. Found both motor overloads open, reset overloads. Motors came back on, compressors and all CFM now operating. Let compressor run while working on another compressor. Checked back on compressor, compressor tripped again. Could not reset compressor. Checked sentronic oil fail, when oil control opens it has 208 v, when oil is closed loses 120v. Need to return and replace oil fail control. Jul 18, 2023 Had part on order but was able to find locally. Replaced sentronic 3 OFC, old pitted Contactor, and auxiliary switch. Re-ran, new L2 wire insulation melted. Compressor now running. Drawing around 38 amps at start and about 28amps running. Replaced 5-amp 250 fuse in B4 switch. All compressors now running. | Compressors/Motors | Compressors/Motors | 0.99826
8/16/2023 4:34:44 AM Mejia, Peter -0001 Sams Club 6619 7/15/2023 Peter Mejia WO# 253771534 Arrived on-site for leaking case checked in with manager on site. Case leaking was medium temp case in online pick up area. Found damaged seals on some of the doors but managed to repair some of them, kinking in seals. Case was leaking from the top of the unit. Found drain evap pan not working and outlet reset was tripped. Pushed it reset button and tested float switch to ensure it was working, it was . Evap pan very dirty and hose clogged, vaccumed and cleaned evap pan and water tested to ensure it worked. Additionally, drain pan for evap coils were very dirty, pulled case and cleaned and vacuumed them. Water tested and no further leaks were found. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99844
On-site 1830-2100 Arrived on site. Checked in with manager, Kristin bc Made way to cases d4.1a/b Case 4.1b high temping due to frozen evap coil Plastic cover panel at bottom of case was hanging off and corner was stuck in the fan blade causing fan to stop running Removed panel and fan turned on and ran normally Removed back panel to access coil and used hose to deice Cycled case back on and temp dropped to 30° Both cases 4.1a/b are at 30° and operating properly Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99816
8/11/2023 12:29:57 PM Paruleski, John -0001 0900-0930 travel 0930-1130 Called for rack B compressor offline Met with manager Jen Inspected rack and found compressor B2 offline Checked and found compressor off on oil fail. Verified comp not full of liquid, restarted and checked ops. 45psi Net oil pressure. All ops check good | Compressors/Motors | Compressors/Motors | 0.99855
8/3/2023 7:06:53 AM Alvarado, Christopher -0001 Checked in with manager Wo order placed so they could order curtain. Closing out ticket per manager. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9957
8/19/2023 7:17:15 AM Maldonado, Chris -0001 Start time-0845 End time-0930 complete check in with manager Kenny checked cafe cooler temp running above 70 degrees checked breaker, and coils to make sure not cooler. (No issue) got roof access located MTRCU1 shut off on high head cleaned coils and raise psi from 350 to 380 checked temp running at 30 checked out with manager kenny | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99591
8/7/2023 De la Cruz, Adrian -0001 8-4-2023 Adrian De La Cruz Jr GP#230803-0103 Po#252730475 Checked in with store manger. I went to the automotive area first to investigate where the leak was coming from. Then I got access to the roof hatch so I could head up to the roof and see the swap cooler on the automotive area that was leaking. When I approached the swap cooler I discovered the float were damaged and had water corrosion. There was too much water in the swap cooler so I had to let it drain out so I could get the proper water levels in the swap cooler. Which should be a half inch from the water drain spindle. Because of the water floats not being operational it was causing the water to drip down to the automotive area. I went to United parts house and order 2 3/8 floats to install into the swap cooler so we could get proper water flow through out the unit. I got back from United after picking up the parts I installed both 3/8 floats.I shut off the power and the water hand valve before installing new floats. Once I was completed with the new 3/8 floats I turned back on the power and water hand valve. Swap cooler was operational. -Job complete | Capital Replacement | Capital Replacement | 0.98799
1530 -1900 pm (3.5 hours OT) Was already on site at provo. Me and other technician Jose went to fix case C11A and C11B. Found cases iced up and Temps were reading very high. There was no air flow in case. Took all product out of case and took case apart. De Iced cases and found the Discharge air temp sensor was broken and was reading over 100 degrees. Went to rack house to confirm if the temp was reading. Came back and put own temp reader and it was reading 34 degrees. Found another sensor on site and replaced it. Case is back to temp and is working great. Checked out with Manager Paul. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99849
8/13/2023 8:30:45 AM Dias, Kenneth -0001 Arrived at site at LTB 3 case fans were not running checked power going into case had power checked electrical Clixon was not on the line re installed it and fans came back on waited for temp to reach set point Case is in temp | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99695
8/1/2023 6:37:32 PM Romero, Gabriel -0001 8/01/23 06EZ7753GARP 3222GE2568 -Arrived on site and checked in with MOD and into service channel. -Accessed motor room and found rack MTB. -Suction psi between 58-62 upon arrival, cut-in setpoint at 56psi. -Verified suction pressure at transducer, 62psi. -Found one compressor toggled off and labeled “bad compressor”. -Rack needs all compressors online to get to suction pressure. -Will need a quote for compressor, contactor and auxiliary, low high pressure switches, 2 techs, 10hrs each. -F/u to r/r compressor. -Job incomplete. 10/4/2023 10:19:35 AM Soto, David -0003 MTB -Arrived on site and checked in with store -found compressor had already been swapped out -appears to be have done under warranty by another contractor -contactor auxiliaries and pressure controls were all still original and not changed out -removed and replaced contactor and auxiliary -pressure controls not available until oct.31 -see 2nd tech notes for further information 10/4/2023 11:12:21 AM Romero, Gabriel -0002 10/04/23 -Arrived on site and checked in with MOD and into service channel. -Accessed motor room and found rack holding suction psi. -Checked comp B3 and found compressor had already be replaced by cool sys. -Noticed contactor still needed to be replaced. -Turned off power to the rack and changed out contactor and auxiliary. -Restored power to rack and slowing cycled compressors back on. -Noticed pressure switches still needed to replaced also. -Will return compressor to United in Buena Park. need to replace pressure switches job incomplete? | Compressors/Motors | Compressors/Motors | 0.99857
8/7/2023 12:20:28 PM Oertel, James -0001 Found a bad time delay relay on compressor number 4 . I had the part on my truck , grainier pt number 1YDD4 Truck 8037. Job complete. Rack A | Compressors/Motors | Compressors/Motors | 0.99854
Arrived on site checked in with manager Got back with novar and continued to try and locate the low temping case ID LT-SC SD FF2a. Still cannot locate the case after speaking with store manager and novar. Found the blueprints for the store and was not able to locate via prints. Main store manager is not available to answer phone due to traveling. Continued to look for case and go through controller and went onto roof checking all self contains for issues. Case is not able to be located. Spoke with service manager and field supervisor both are in agreement this call will be closed out. Did last check in the curbside and cafe areas and case is not to found. Updated manager call is complete | Nuisance Calls | Nuisance Calls | 0.99801
Arrived at the store, logged into Service Channel and spoke with the manager, Christine. I looked over the rack and found compressors were working and temperatures are coming down. I was advised that someone had already restarted the compressors because they were off from the plumbing work that was being done on the cooling tower. I spoke to Christine and told her what I did and what I found. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.9973
7/28/2023 9:14:02 AM Moran, Greg -0001 Inspected fan covers. Ordered 4 new fan covers. 8/22/2023 10:06:06 AM Moran, Greg -0002 Incomplete Parts on order!! 8/25/2023 2:13:45 PM Young, Roderick -0003 Incomplete 9/14/2023 3:52:09 PM Lawson, Christopher -0004 Completed Checked in with manger on site went to meat prep room replaced fan guards no other issues found | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99747
8/17/2023 11:45:42 AM Martin Jr, Robert -0003 Installed new door gaskets through out the store on the walk in freezers/coolers and adjusted doors. There are still some that need new torque rods, another tech has some on order on another work order. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99732
8/16/2023 9:43:57 AM Stark, Keith -0001 Found compressor locked out on oil. I reset compressor. Compressor is running properly | Compressors/Motors | Compressors/Motors | 0.99837
8/2/2023 8:12:57 PM Martinez, Alexis -0001 Checked in with Anthony Checked out with Anthony RTU 16 Brand: Lennox Model: LGE060HH1G Serial: 5603G05645 Reason for call: RTU 16 Office A/C running warm Upon inspection of unit found unit to be off Proceeded to check for power at the unit Found power and disconnect to meet specs Initiated cooling using Tool called jumper king Cooling went to effect Called home office Home office said that hvac for job site is unavailable Proceeded to electric room down stairs near office Found RTU device reader Found Rtu 16 in comm loss Proceeded back up stairs and reset novar control board Cleaned board with brush to get rid of dirt debris build up Plugged everything back in and unit was now online Proceeded back to office Office was now cooling down and no longer running warm | Nuisance Calls | Nuisance Calls | 0.99791
7/20/2023 6:07:22 AM Delgado, Jesus -0001 Return to site check in with manager. Mike was shown case aso6 not maintain proper temperature replace CDS valve on as05 will return and follow up. This call is not complete Parts used CDST-4 7/20/2023 11:47:37 AM Delgado, Jesus -0002 Multiple failures may be due to power outage, power cycling, controllers, Check in with management on arrival call digital assets/Novar tech-support. Multiple times call kept getting disconnected. Novar, Tech Support configured staging of compressors on rack A secondary compressor s3 not staging on due to CT board Not reading amp draw went through multiple troubleshooting procedures with tech-support determine CT board needs to be replaced. Board not Allowing suction pressure to maintain. Explain to management will return with new board. This call is not completed. 8/19/2023 12:54:32 AM Delgado, Jesus -0003 CT board was replaced on other work order 230811–0056. Service channel 253489054 Temperature at case AS05 and AS06 is now maintaining proper temperature made adjustments to controller. Continue to monitor ensure case temperature maintains average of 35F. Satellite compressor 3 has not tripped for alarm after replacing CT board this call is now completed cases are both reaching set point | Compressors/Motors | Compressors/Motors | 0.99846
8/10/2023 Found that the wi cooler is off for the bakery. Called store support and had them suppress the alarms for 1 week to allow them time to finish the floor. And stop anymore automated work orders from being created for this walk in . Everything is working properly. | Nuisance Calls | Nuisance Calls | 0.99825
8/8/2023 4:30:03 PM Fierro, Steve -0001 Sams Club #6619 -Ontario Systems:DTC-Comp 6 C.S.: 230808-0173 P.O.: 253230762 —————— 8/8/2023 Steve Fierro TT/ST:1330-1430 Time In:1430 Time out:1630 Checked in with MOD Got roof access Located DTC Looked at controller alarms found Primary C06 locked out on oil Located compressor Found sight glass at oil float half way full Reset compressor and monitored run time Checked net oil pressure Checked restriction @ oil separator Sight glass on oil reservoir full Checked for any restrictions at filters/ driers Compressor did not lock out again Tightened connections at contactor and auxiliary they were half a turn loose Call complete | Compressors/Motors | Compressors/Motors | 0.99864
7/21/2023 5:41:17 PM St. Amant, Kenneth -0001 Sam’s club #: 6619 System: cafe freezer SC: 230720-0317 PO: 251406123 —————— 7/21/23 Kenneth St.Amant Checked in with manager Arrived on site checked in with location gained access. When to the cafe freezer and it was off When to the roof checked gas and psi and it was good To Look at the DEFROST TIME CLOCK and it was bad Put new DEFROST TIME CLOCK time in and the cooler kick on Put it in defrost to make sure it goes into defrost and comes out and it does Cooler is back running and good Checked out with manager Kelly Job completed | Nuisance Calls | Nuisance Calls | 0.99784
Arrived to store located fan making noise found that wire was hitting fan blade causing noise. Had to remove fan to repair wire. Was able to install fan back and keep wire away from fan blade. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99702
7/19/2023 2:51:31 PM Zaun, Paul -0001 7-19-23 Paul Z / ventilation motors out on rack B Rack B checked in with Jeremy found motors not running called supply house located 1 and orders other 3 will replace all run capacitor also Replaced one motor and two capacitor today follow up on Monday when parts arrive Incomplete 7/24/2023 8:10:39 PM Zaun, Paul -0003 7-24-23 Paul Z / FU to install ventilation fans checked in with Jeremy picked up parts from supplier house returned and installed fan motors and replaced capacitors on other motors all motors are working at this time job completed | Compressors/Motors | Compressors/Motors | 0.9983
Cody warden 7/25/23 Travel-0945 Arrival-1000 Departure-1230 Responding to unit not “blowing” in fuel hut. Checked in with manager/Jacob APw/ Mcclean Model cr43-08-16-051 Serial 0215508544-3 Inspected return to find there was no filter in place. Coils were badly plugged. Checked refrigerant pressures which were a little low. Verified operation of blower for correct voltage and amperage which were both good. Cleaned condenser coils and the evaporator coils to ensure proper airflow to efficiently cool and condense refrigerant. Checked out with manager/ Lamont Turner Job completer | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99777
Found all compressors on rack b running. Discharge pressure is running at 345. I shutdown the rack and condenser. I washed out the condenser coils. Head pressure is now running at 265psi. All cases are now down to temperature. | Compressors/Motors | Compressors/Motors | 0.99836
7/20/2023 8:06:04 AM Brooks, Byron -0001 Time in: 1515 Time out: 1700 Checked in with MOD Went to Dr. office A/C didn’t seem to be running and was hot in there Accessed roof Went to RTU 22 and RTU 14 above dr. Office Both compressor off on high pressure and fans not running Reset compressors and got them running as well as the fans Condensers on u it’s extremely dirty Washed off condensers Went back into building to go to dr. Office A/C back on and cooling office Checked out with MOD Call complete | Compressors/Motors | Compressors/Motors | 0.99845
Sam club #: 4709 System: MTB-15 SC: 230807-0291 PO: 253157564 —————— 8/7/23 Kenneth St.Amant Travel-13:00-16:45 Onsite-16:45-18:30 Checked in with manager Arrived on site checked in with location gained access. Took case apart and found the left fan unplugged So I took the back panel off to make sure it was not ice up Manager wanted one of the employee to clean the case really fast before I put it back together So once the employee was done cleaning the case I put the case back together and case it at 35° Checked out with manager Sonia Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99793
TTOT 1945-2015 Time in 2015 Time out 0000 Rack C M# PS S# 120037 Tg# 0090050 Checked in with manager Francis There were no alarms all day for these curcuits on controller. There were no active alarms. All these circuits were still running at 49 degrees. The solenoid for subcooler on rack was not energizing properly. Subcooler needs to run all the time during these high ambient temperatures. Subcooler temperature sitting at 98 degrees and no alarms on subcooler controller. Opus operates the solenoid. I bypassed solenoid so it will energize constantly. Subcooler temperature dropped and all temperatures dropped. All circuits on ticket now at 35 degrees. Checked out with manager on duty Francis. Complete | Compressors/Motors | Compressors/Motors | 0.99825
8/4/2023 1:13:05 PM Cox, Brandon -0001 Brandon Cox Arrival 1045 Departure 1315 Notified manager(Peter) was here to check on the damaged coil. Found RTU 14 with coil fixed due to micro leaks in coil. Got a plastic bag and electric tape Covered coil to prevent from tripping high head pressure. Need to quote to replace coil. Need a crane 35 feet up and 30 feet in. Also need 410A recovered Coil changed out. Charge system back up and check ops. Call not complete. 11/7/2023 12:59:18 PM DiCecco, John -0002 John DiCecco 11-7-23 Travel 0515 Arrive 0545 Depart 1345 Travel 1430 Checkin Taola Arrived and checked in to service channel. RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call complete. 11/7/2023 9:25:18 PM Pulido, Jansen -0004 Jansen Pulido 11-7-23 Travel 0530 Arrive 0800 Depart 1345 Travel 1430 Checkin Taola Arrived and checked in with TOS, Jake Dicecco RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call compete. 11/8/2023 6:55:15 AM McKinzie, Daniel -0003 Dan McKinzie 11/7/23 Travel 0430 Arrive 0800 Depart 1330 Travel 1430 Checkin Taola Arrived and checked in to service channel. RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call complete. | Capital Replacement | Capital Replacement | 0.98212
GC -Need curtains for LTB 4 or FF3 curtains are damaged and need replaced with lighter duty ones or ones that do not freeze. This is for freezer 3 not a duplicate work order. REFRIGERATION (FROZEN, COOLERS, DAIRY ETC.) / Refrigeration / Strip Curtains Scheduled date: July 23, 202310:24 AM 7/27/2023 12:35:00 PM Sparks, Scott -0001 7-27 Scotty Sparks Travel time 0600-0730 On site 0730-1400 Departure 1400 Checked in and out with Kaytlen Found both POS WIF Needing strip curtains. Removed old strip curtains from both freezers. Installed 2 new sets of curtains. Job completed. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99724
8/16/2023 7:03:52 PM Garreans, David -0001 TTOT 1730-1830 Time in 1830 Time out 2100 Checked in with manager Andre. C01a Hussmann M# F12G S# MY18F043041 Tg# 0031735 There was about 2 feet of case that had no airflow. I valved off case and let it air defrost for a while then turned back on. It now has airflow. No temperature issues. Checked out with manager Benny. Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99711
7/27/2023 2:23:00 PM Kaser, Wade -0002 Arrived on site, called for secondary tech assistance, utilized ladders for door access to control panel, door had no power, found power to door, but door wouldn’t open or close completely. Removed main door panel off, checked all sensors, rolled door down manually, and found large piece of plastic wrap obstructing sensors, put everything back together. Door is now operating as should. 7/27/2023 4:32:28 PM Arriaga, Luis -0001 Assisted tech Wade | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9966
Parts needed. Incomplete. Please order. Checked both bakery freezer doors. Recorded information needed for expediter to order safety strap assembly’s for both bakery freezer doors. Please see attached photos and information below. Roll Seal Door RS500 Model 6421-2281 Serial number 0004219 Need safety strap assembly only 2 techs 4 hours each Roll Seal Door RS500 Model 6640-12112 Serial number 00003600 Need safety strap assembly only 2 techs 4 hours each | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9967
Aug 07, 2023 Freezer was off at 75°. Found freezer full of water and water dripping from ceiling and walls. Freezer and cooler sight glass flashing. Found broken fire sprinkler went off in freezer, water got inside EFM and shorted. Found 1 leg of power missing from control circuit for fans. Power cycled and unit came back on. Fans are now on. Replaced fan, used EFM D1125 Fasco from truck stock. Leak checked w/electronic sniffer; no leaks found. Used tape to tape up hole where fire sprinkler was removed. Wiped water from ceiling and walls, squeegeed water from floor. Both fans came on, box dropped to 12° and went in defrost. Will return tomorrow to check temp. Aug 08, 2023 Found box at -10°, at temp. System operating normal, no more issues found. | Damage by Customer | Damage by Customer | 0.9468
Onsite 1915-2000 Rack B low receiver level-while onsite I checked receiver level it’s at 30% I torch receiver to make sure gage was working did not find any issue I informed MOD of job performed and checked out | Nuisance Calls | Nuisance Calls | 0.99837
Jul 20, 2023 Checked WIF and found the pvc drainline disconnected from the wall. Drainline was clogged, missing the floor drain and the pvc was missing struts. Acquired parts and installed new strut/bolts. Drainline is cleared and good. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99831
No travel: On-site: 1400-1700 On arrival checked on with store manager. Stated that the grab and go cooler is running warm. Verified i had air flow and all evap fan motor are working properly. Went to roof top to locate remote condensing unit -3. Found condensing unit it off and and after inspection found that i had a bad contactor. Went ahead and replaced contactor with new and started up unit. Verified unit is now running and clear aight glass. Monitor case and temps are back at set points. Notified manager about findings and CALL IS COMPLETE. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99707
Andrew Debeaulieau 8/4/23 Travel 0715 Arrival 0830 Departure 1300 Kysor-Warren OIV5V14-03UN 0809001756 Checked in with service channel. Shown case A-5C reach on frozen food. Case is iced up, turned off liquid line hand valve. Had home office initiate defrost. Defrost heaters 5.7 amps Pulled case apart to deice, found 2 defrost heaters unplugged behind fans. Plugged in heaters and Deiced coil. Heaters now 8.7 amps and individual heaters that were unplugged now drawing 2.9amps each. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99854
7/17/23 Upon arrival checked in with manager: maryah Tech checked break room airflow/ No airflow Tech gained access to rooftop Tech located : RTU 1. / RTU 16 both not working Tech checked contactors / No 24volts Tech cleaned both condenser coils with water Tech checked all safety switches Tech checked for bad connections Tech reset hi pressure switches Tech gauge up to compressors and checked pressure Tech checked blower motor/ Belt broke Tech installed new blower motor belt on unit Tech has both :RTU working and making temperature Tech checked out with manager : Maryah Make : Lennox Model No. LGE060HH1G Serial No. 5602M04982 Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99702
7/18/2023 7:35:49 AM Lopez, Miguel -0001 Incomplete, waiting on parts. Arrived onsite, checked in with manager. Assisted tech on site with LTA4&5 work order. Assisted tech with scissor lift to adjust freezer door. Inspected issue. Door in need of new Gasket. Adjusted track to resolve, Door overall falling apart from forklift damage. New door recommendation. Emailed willie measurements and serial number. 76inx 108in 8/8/2023 8:14:46 PM Lopez, Miguel -0003 Incomplete Arrived onsite, waited on Sam’s employees to move pallet for door and rail track. Unboxed rail and door. Went to door needing replacement and began uninstalling process. Used ladders to unhinge walk in door. And uninstalled old railing track. Waited on forklift operator to help carry door out to receiving. Forklift operator help move new door to site. Brought old railing out to outside receiving. Began installing new railing. Used scissor to install. Cleaned up package trash. Will return Wednesday with trailer to pick up door and crates. 8/9/2023 1:48:27 PM Lawson, Christopher -0002 Completed Checked in with manger on site went to lta 2 freezer adjusted door and fixing wiring for heaters then cleaned up and hualed old door off and pallet box it was in no other issue ncomplete Checked in with manger on site went to LTA -2 freezer replaced sliding door and door track eith all brand new hardware no other issue found will return tomorrow morning to pick up old door 8/10/2023 8:48:03 AM Lopez, Miguel -0004 Completed Arrived on site, Picked up uhual needed to remove old door and crate. adjusted door electrical wiring for heater, adjusted door height and door handle to appropriate levels to ensure seal. Returned to trashed out back, loaded up uhual with old door, and it’s crate. Returned to shop to trash items. Recycled door. Return rented uhual trailer. Returned to Sam’s to check out. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9972
Arrived at the store, logged into Service Channel and spoke with the manager Alfred. I looked at A2 compressor and found that the breaker is tripped. I turned breaker off and checked through the electrical and found a burnt wire in electrical box on top of the compressor. It looks like the overload is fried so I will order a new overload. I spoke to Alfred and told him I will leave this work order open. | Compressors/Motors | Compressors/Motors | 0.99856
07/18/23 Mario A Sams 4824 W 230714-0222 Travel : 0830 Time In: 0930 Time Out: 1830 Complete Arrived onsite check in with a manger on duty for repairs on Air Cool Tower -Removed and installed 4 new replacement CFM -Check amps drawing @ 2amps -Discharge @ 307psi / with replacement motors discharge @ 263psi -VSD back to auto Complete | Compressors/Motors | Compressors/Motors | 0.99845
Completed. Received part that needed installation. Located meat case that was missing the piece, case was being stocked at the location of the missing piece. Once stockingu was completed, I removed the black plastic bumper enough to put new piece in, removed tape covering metal piece. Once in place, I lined up the holes to put screws in. Put plastic bumper back in place and made sure metal piece was all the way in place. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99661
8/3/2023 8:49:22 AM Cochran, Lila -0001 Complete. Assessed door adjusted both top and bottom brackets on door. Had to make several adjustments. Door working properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99725
8/7/2023 9:03:42 AM Gary, Raymond -0001 8/7/23 Ray Gary Arrived onsite and checked in with the manager Went to The rack house a Found the receiver around 12 percent Because of the alarm I did a visual and electronic leak search Found nothing to raise my concerns So I went to the cases and did an electronic leak search on each case Got no hits I called Sams Monitoring and spoke with Carlos And he said it wasn’t in alarm any more THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99812
7/25/2023 11:40:26 AM Harguindeguy, Joseph -0001 7/25/2023 JH -upon arrival checked in with store manager -shown drain pipe dismounted from wall -picked up parts from parts house -returned to store -remounted drain pipe into wall -checked out with store manager | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.98973
GC -LTB2B Looks like the entry door got hit, won’t close unless slammed REFRIGERATION (FROZEN, COOLERS, DAIRY ETC.) / Refrigeration / Walk In -Freezer Equip: X-STS18GBSARWW-Demo Room-6632, Brand Other, Model #STS18GBSARWW, Serial #LH785854 Scheduled date: July 27, 202310:15 AM 7/25/2023 5:01:58 PM Sparks, Scott -0001 7-25 Scotty Sparks Travel time 0745-0815 On site 0815-1800 Travel time home 1800-1830 Checked in and out with Leo Checked opes on door. Store hit new door with a pallet jack. Had to realign wall and secure wall. Readjust door. Realigned door strike. Door works like it’s supposed to. All opes ok. Job completed. | Damage by Customer | Damage by Customer | 0.98613
7/19/2023 6:19:23 PM Robak, Anthony -0001 Anthony Robak Checked in with MOD Carla Went to rack house for compressor lockout found on ticket 221227-0012 Found rack running critical suction but all circuits at temp Found compressor 1 in oil lockout, 4 off on head pressure, and 5 off on amp protection, Reset comp 5 and found it pulling 75 amps on start up and maintaining 55 amps when running over time span of 5 minutes Amp draw is too high Compressor 5 is bad Pumped down compressor one and checked oil transducer screen Checked comp 1 oil screen and found it severely dirty Cleaned screen Comp 1 maintains good oil pressure Checked contactor and found it severely pitted Changed contactor with DP350240 Comp 1 back online Reset compressor 4 after cleaning condenser on separate ticket Rack running at suction setpoint All circuits at temp Will order compressor 5 Model Carlyle 06ER4756SO Checked out with Ryan parts on order 8/4/2023 6:29:50 PM Oertel, James -0003 We replaced one compressor and will return to replace the second 8/4/2023 10:10:49 PM Maldonado, Chris -0004 Start time-1730 End time-2345 arrive to assist with compressor change out 8/5/2023 12:17:22 AM Toomer, Collin -0002 230719-0255 ST15:30-16:00 OT:16:00-00:00 8/5/23 OT:00:00-00:45 OT TT:00:45-2:15 arrived checked in With MOD gained access to Rack A, M&S picture attached valved off compressor #6 dumped remaining gas into suction header, removed compressor Installed new compressor. pulled vaccum to -30hg and performed decay test. leak checked compressor with bubbles and stratus, no leaks at this time. Opened valves back up fully and started compressor checked all safety’s and amp draws on start up. Everything running properly at this time. will follow up and recheck for leaks next week when I return to do compressor #5. pulled two gallons of POE oil off of truck 8036 (Jim) and input into compressor. Job complete. Checked out with manager. Just realized I’m on the wrong ticket compressor #6 was replaced on this ticket not compressor 5 we will be replacing compressor #5 next week on 230207-0113. | Compressors/Motors | Compressors/Motors | 0.99853
Job completed Adjusted the bottom of the freezer door with the bottom toe kick plate and also adjusted the top track to close the gap on the opening side | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99706
7/27/2023 7:46:19 PM Caraballo, Marcos -0001 Meat prep C6A and C6B At arrival checked in with store manager Located meet prep high temping Began, deicing, frozen coils After all ice was cleared Went up to rack to check perameters Found that the system had no defrost cycle scheduled Spoke with Home office they were not able to set parameters for defrost Technician to follow up in the morning to set parameters/speak with novar systems This call is not complete Temperatures at departure, 46° Checked out and obtain signature from manager Kiahnah 7/31/2023 6:07:02 PM Edwards, John -0002 MTPR System C6a,b NOn arrival checked in with MOD. Called home office and confirmed parameters. Defrost set to 4x45. Prep area at 50 and coils clear. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
Curbside 3 door cooler On the right Time in 1600 Time out 1830 8/03/2023 Robert F & Bill L Already onsite checked into ivr and with mod. Accessed curbside pickup and 2nd cooler has last door on the right has broken hinges. Called to get second tech to drop door and remove broken hinges. Fished out bottom hinge stuck inside door. Then installed bottom and top hinges and adjusted torque for proper closing. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99714
8/4/2023 2:26:18 PM Reyes, Ruben -0001 Condenser A Checked in with store manager Rebekah Access motor room and check condenser A operations Control by VFD condenser fan motor number two seized and condenser coil plugged pump down both racks toggle off compressors and power off condensers removed fan guards and wash condensers coils from top and bottom assemble and restarted Located replacement CFM and picked up Remove and replace condenser fan motor number two Pulling 1.7 amps per leg all condenser fan motors online suction pressure 14 psi discharge pressure 260 psi R404A Job complete | Compressors/Motors | Compressors/Motors | 0.9983
7/28/23 TH Time in: 16:30 Time out: 17:00 MTC-1 Heatcraft MN: WKE270BEC SN: T18H02102 Arrived on site and Checked in with Service channel and MOD(Hilda). This call is duplicated call. Reference PO#251495817. Informed and checked out with MOD(Hilda) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99844
Found lta4a evaporator vibrating heavily. Both fan mounts have cracked. I’ve shut lta4a and b evaporators off. Lta5a and b are still up and running. I will return to repair the brackets or order them. | Compressors/Motors | Compressors/Motors | 0.99604
Arrived on site checked in with manager, gained roof access Located pharmacy RTU 23, found that the condenser fan motors wouldn’t turn on during cooling causing the compressor to go off on high head pressure After further diagnosing I found that the fan motors weren’t receiving power, after tracing the wires back I found that the electrical connectors at the contactor and capacitors were loose and not making proper contact Replaced connectors, and tested operation, Return air reading at 83 degrees and supply air reading at 54 degrees, called home office before checking out and zone temperature was 71 degrees on departure Call complete checked out with manager Trevon I did notice the the air filters were dirty, I recommend getting them replaced in the near future(picture in attachments) | Compressors/Motors | Compressors/Motors | 0.99859
7/17/2023 1:37:56 PM Hanamornsate, Thirathanawat -0001 7/17/23 TH TT: 8:00-9:00 Time in: 9:00 Time out: 10:00 MT-BS-1-B: HUSSMANN MN: ID5SM12 SN: MY18F044846 Checked in with Service channel and MOD (Alex). Checked the location. The case is good airflow. Checked the monitor. The case is at temperature (31 Degrees F). Checked history alarm page and No found alarm on this case. Checked graph temp is good. Informed and checked out with MOD(Brad) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99842
Dan McKinzie 11/7/23 Travel 0430 Arrive 0800 Depart 1330 Travel 1430 Checkin Taola Arrived and checked in to service channel. RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call complete. | Compressors/Motors | Compressors/Motors | 0.98697
7/16/2023 4:50:43 PM Ried, Nicholas -0001 Completed. Checked in with management. Accessed rack A and found no issues. Checked controller and found all freezers at temperature. The door may have been open for a long period of time during a defrost. Same issue with the snack bar freezer. The door was left open. Freezer maintains 0 degrees when the door is closed. While on site I adjusted the door for POS refrigerator. The door now slides easily. No further issues. | Nuisance Calls | Nuisance Calls | 0.99818
07/24/23ZP SAMS CLUB 4704 Condenser A & C -Got access to racks. -Pumped down rack C and shut off the condenser. -Began to wash out the condenser. -Turned the condenser on afterwards to dry it out and cycled the rack back on. -Pumped down rack A and shut off the condenser -Began to wash out the condenser -Turned the condenser on afterwards to dry it out and cycled the rack back on. -Waited for all case temps to drop. -This call is now complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99517
Check in with manager Mike, on arrival was shown endcap was told case B 11 had poor flow Notice display case, showing clean mode. Reset, controller under case with no change cycle through parameters manually force from clean mode to refrigeration. Chase is now displaying temperature and is refrigerating. waited for case to reach setpoint of 30f. case now has airflow all at normal at this time Explain to management this call is completed | Nuisance Calls | Nuisance Calls | 0.99791
7/24/2023 5:04:39 PM Garreans, David -0001 TTST 1200-1230 Time in 1230 Time out 1800 Rack C M# PS S# 107351 Tg# 0028297 Rack was pumped down at CDS valve coming off subcooler providing liquid for liquid header. The Novar subcooler board was not working. Checked wires, found power wire loose on board. Tightened power wire on board and board started up, CDS valve opened and rack started up. Temperatures all dropped. Monitored operation. Helped Jim out with rack B. Checked out with manager Jamaily. Complete | Compressors/Motors | Compressors/Motors | 0.99839
8/1/2023 9:17:07 PM Barajas, Armando -0001 Job completed. Arrived on site and found the compressor running. Went through the Novar board and found that the compressor tripped a couple days ago. Found the sight glass low on the compressor. Went to the reservoir and found it empty. Began checking pressure on my oil line and found a dip in pressure across the oil filter. Picked up new oil filter for the rack. Pumped down the oil line and isolated the filter. Changed out the filter and filter gasket. Put the filter back together and opened up the oil lines. Added one gallon of oil to the rack and confirmed the reservoir began filling up. The compressor is online and the rack has a sufficient amount of oil now. | Compressors/Motors | Compressors/Motors | 0.99849
8/18/2023 1:01:13 PM Martin Jr, Robert -0001 Found compressor 1 on rack A tripped on high head. All fan motors are currently running on A rack. Discharge pressure is reaching 340 during the heat of the day. I highly recommend changing out the condensers on A and B rack. They are deteriorating. Reset compressor and it came back online. All compressors are currently running. Adjusted the head pressure control on comp 1 also. It was set at 300 and I moved it up to 375psi. Compressor stayed running. Discharge is currently 305psi. Washed out condenser and it helped a little bit. Condenser really needs to be replaced. | Capital Replacement | Capital Replacement | 0.98524
Andrew Debeaulieau 7/25/23 Travel 0445 Arrival 0815 Departure 1500 Upon arrival found large oil stain and puddle outside Rack B side of motor room. Found Compressor B2 has leak on oil line to oil regulator line. Isolated and attempted repair with copper gasket; did not fix. Ordered new parts, leak section is isolated from rack. Cleaning up oil spill from leak while parts are enroute. Replace elbow between oil regulator inlet and angle valve on oil line. Used nylog and copper crush gasket to insure leak free seal. Check fitting with leak detector and confirmed repair complete. No other leaks detected at this time for Rack B. | Compressors/Motors | Compressors/Motors | 0.99855
8/15/2023 5:05:39 AM Cosgrove, Reese -0001 On-site 2230-2400 Arrive on site. Checked in with manager, Chapra Model: 03.5UM6 Made way to grab and go case for cafe, MTCU1 Removed drinks from cooler Removed panels to access evap coil Found evap coil iced up Also noticed water leak on floor around cooler Main drain line is clogged, informed manager that plumber needs to come out and fix the drain. Manager requested that we come back to diagnose as they are closing the store for the night. Incomplete follow up Returned 8/14 Arrived on site. Checked in with Shaik. Condensing unit model: BHT015X60 serial: T10B05108 Made way to rcu1. Cycled power on Evap coil is thawed out All fans are running Noticed manual valve was not open all the way Open valve completely Suction pressure @ 71psi Cooler temp is down to 36° Tested defrost cycle and ensured proper operation Cooler is operating properly Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99828
7/31/2023 6:03:19 PM Hernandez, Rodrigo -0001 Bakery freezer roll seal door not closing Had to remove poles and straighten out tarps Found safety strapped was pulled all the way down causing door to not properly open/close Adjusted strap to correct length Checked all ops and parameters Adjusted down speed lower to prevent tarp from getting stuck Found home switch flipped wrong way, adjusted switch direction Strapped down strap to prevent anyone from pulling strap down by accident to prevent any more calls for this door Checked all parameters and ops Door is now properly closing and opening with no issues Checked out with mod Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9954
7/31/2023 3:03:05 PM Villemaire, Ryan -0001 Arrived to location, checked in with Greg. Found circuits b05, b03a and b03b at setpoint of 28. Checked graph found graph spike at the same time management was conducting case cleaning. Management sent an email to Monitering stating they will be turning ball valves off at case in order to properly case clean. Ball valves were turned off, case was cleaned whilst happening temps spiked. Cases are now operating to standards and are at setpoint. This lineup will be cleaned every Sunday night due to it being fresh meat would recommend a note be put in for this store to avoid unnecessary calls being put in. Call completed, checked out with Greg. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99715
Hussmann Model: RL-3 Serial: My12A000832 System: LTB-7C Checked in with manager then began checking the RIFF case. System B7c was temping high. Checked the coil for ice buildup and verified the fans were running. Checked the txv and found it was frosting at the body which can indicate there is a restriction in the screen. Pumped the system down and swapped the txv screen for a new one then turned the system back on. Went to the motor room and began checking the rack. Found compressors 2 and 3 were off on oil failure which was causing issues with the suction pressure. Verified the compressors had oil in them then reset them both and verified operation. Checked voltage and amp draw for each compressor then gauged up to the compressors and checked oil pressure. Both compressors are showing 70-80psi net oil pressure. Checked the oil reservoir and found it had 2 balls floating. Monitored rack operation and waited for the system to drop to temp. The case quickly dropped below 0 and is running well. Checked out with manager, call complete. | Compressors/Motors | Compressors/Motors | 0.99834
found fan stuck in ice for break room freezer. found drain plugged and ice building up from drain lime. we de iced drain line. ran freezer through a defrost all heaters working and drain heater working. put case back together and freezer is back down to 0 degrees and dropping. while onsite i had novar program comp 5 for A rack from Normaly open to normally closed. comp 5 now back online for A rack. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
7/31/2023 6:16:54 PM Angelle, Troy -0001 Found compressor 2 running properly and compressor 5 is turned off and has parts on order. 9/11 Tech Troy advised: From: Troy Angelle tangelle@arcticomgroup.com> Sent: Monday, September 11, 2023 8:34 AM To: April Harper aharper@arcticomgroup.com> Cc: Melissa Sarabia msarabia@arcticomgroup.com>; Devin Weber dweber@arcticomgroup.com>; George Albritton galbritton@arcticomgroup.com>; Kate Granger kgranger@arcticomgroup.com> Subject: Re: WO 252268442 Shipping/Tracking Information Required I’m here now for another call and the repairs were done on another ticket so this one can be closed..MS | Compressors/Motors | Compressors/Motors | 0.99867
7/15/2023 1:22:47 PM Duarte, Juan -0001 7/15/23 Travel:10:45-11:15 Onsite:11:15-12:00 Checked in with manager Diana upon arrival. Found glass on freezer door cracked. Cover door with cardboard and got info needed for new door. Will submit quote for new door. 1 tech 6 hours 1 door 1 torque rod 1 torque master 1 hinge pin. 8/22/2023 6:41:27 AM Emmer, Bob -0002 8/21/2023 Bob E Tech picked up door and parts and drove to location. Tech check in with service channel and store manager on arrival. Removed damaged door and installed new Anthony door. Adjusted door swing. Tested door multiple times. Door now working properly and sealing properly. Tested anti sweat heater and is working properly. Job complete Also took broken door for disposal. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99714
7/20/2023 5:12:39 PM Romero, Gabriel -0001 MTB RCU3 -Arrived on site and checked in to service channel and in with MOD. -Located dairy coolers temping warm and didn’t find anything wrong with evaporators. -Gained roof access and located condenser associated with RCU3. -Found compressor offline with no power to unit. -Traced power back to electrical panel and found breaker for RCU3 tripped. -Tested compressor terminals to ground to verify compressor was not ground. Compressor ok, not ground. -Checked windings at compressor and got continuity. -Tightened all electrical connections and verified no burned wires. -Reset breaker to RCU and monitored system ops. -Case temp dropped and compressor and condenser fans working properly at this time. -Suspect breaker may be going bad and will need to be replaced. -All system ops ok at this time. -Job complete. | Compressors/Motors | Compressors/Motors | 0.99856
Found compressor 2 running properly and compressor 5 is turned off and has parts on order. | Compressors/Motors | Compressors/Motors | 0.99853
Checked in with mod. RCU 3 not cooling Checked unit and found it off on high head pressure switch. Reset unit and checked pressures pressure is within range unit tripped on high head due to record high ambient temperature | Compressors/Motors | Compressors/Motors | 0.99807
Checked in with Matt then began checking rack B. Compressors 1 and 3 are both cycling normally and appear to be running well. Gauged up to each compressor and verified the oil pumps were working correctly. Checked pressure safety settings to ensure they were correct. Checked voltage and amp draw on each compressor and found they were both running well. Verified the compressors had oil in them as well as oil in the reservoir. The rack is running well and maintaining setpoints. Checked out with Matt, call complete. | Compressors/Motors | Compressors/Motors | 0.99858
7/17/2023 5:58:06 PM Stuart, Christopher -0001 En Route: 1630 Time In: 1745 Time Out: 1945 Comp B-2 L/O (Home Office Alarm) Gained access to Rack B. Comp 2 was online at arrival. Rack pressures @ 50/258. Outdoor ambient between 105-110 and could have caused the condenser to spike high side pressure, causing comp to temporarily lockout. Monitored compressor for awhile. No further issues found. Job Complete | Compressors/Motors | Compressors/Motors | 0.99867
8/17/2023 2:34:05 PM Haddad, Masoud -0001 Arrived on site checked in with the manager mentioned the beverage case by the cafe not working -hussmann model #ID5SM6 serial #MY19B012280 case #B14 -found the evaporator iced up -went up to the roof to the condensing unit and after troubleshoot found the defrost timer bad and not turning automatically -drove to a local part shop and got a defrosted timer -went back to site and installed the defrost time and the unit start to go to defrost -de iced the evaporator -manager said after we got power outage this happened -the defrost shorted because of the power outage -all checked good and the temperature dropped normally -call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
7/22/2023 9:34:33 AM Ceja, Mario -0001 Arrived on site checked in with manager (Mike) and service channel . Located B06a ice cream case . Cases on arrival at -5 . Found no issues with cases . No ice build up all fans running . Good airflow . Checked door gaskets and door tension to make sure they close properly. Found no issues . Case was either being stocked with product or customers left door open . Case temp on departure-5 . No further issues . Job complete 1000-1030 travel OT 1030-1130 labor OT | Nuisance Calls | Nuisance Calls | 0.99784
Checked walk-in cooler at cafe/snack bar and found stuck head master(head pressure control valve). I had to bypass it and install a mechanical head pressure control. I had to recover the refrigerant front the system, remove the head master and install the new control and wire the condenser fan motor to it. I pulled a vacuum on the system and charged with refrigerant. Added 20lbs of R404A refrigerant. No other problems were found. | Compressors/Motors | Compressors/Motors | 0.99813
8-4-2023 Adrian De La Cruz Jr GP#230803-0103 Po#252730475 1000-1030 TT 1300-1330 Lunch check out 1330-1700 on-site Checked in with store manger. I went to the automotive area first to investigate where the leak was coming from. Then I got access to the roof hatch so I could head up to the roof and see the swap cooler on the automotive area that was leaking. When I approached the swap cooler I discovered the float were damaged and had water corrosion. There was too much water in the swap cooler so I had to let it drain out so I could get the proper water levels in the swap cooler. Which should be a half inch from the water drain spindle. Because of the water floats not being operational it was causing the water to drip down to the automotive area. I went to United parts house and order 2 3/8 floats to install into the swap cooler so we could get proper water flow through out the unit. I got back from United after picking up the parts I installed both 3/8 floats.I shut off the power and the water hand valve before installing new floats. Once I was completed with the new 3/8 floats I turned back on the power and water hand valve. Swap cooler was operational. -Job complete | Capital Replacement | Capital Replacement | 0.98788
07:30 -10:30 am (3 hours REG) Arrived on site and checked in with MOD. Checked walk in freezer and found the pvc drain line disconnected from the wall. Drain line was clogged, missing the floor drain and the pvc was missing struts. Acquired parts and installed new strut/bolts. Drain line is cleared and good now | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99815
Upon arrival rtu-10 would cycle on and then cycle off after about 16 seconds. The code showing on the display was indicating that it wasn’t calling for the fan blower motor to come on, this was leading me to believe that someone put the fan on the thermostat to the off position. I couldn’t gain access into the pharmacy due to safety regulations. | Nuisance Calls | Nuisance Calls | 0.9983
Travel: 0630-0830 On-site: 0830-2030 On arrival checked in with store manager. Stated that all cases for rack B are running warm. Went to compressor room and found no compressors running. I immediately got odor of burnt wiring. After investigating found that contactors for comp#1 and #2 were completely fried along with auxiliaries. Checked both compressors for any possible shorts and and found compressor#3 had open windings and compressor needs to be replace. Compressor was still operational condition. Replaced contactor for comp#2. After continuing to troubleshoot found that control voltage breaker was tripped and rested. Once resetting i started up rack except comp#3. Monitored and rack struggled to come down to suction. Saw that compressor 5 for rack was toggled off and check to see if its in operational condition. Compressor was in operational conditions and started up comp. Rack now is holding proper suction. As i am monitoring i noticed that controller had a active low level receiver alarm. Did verify i had no liquid level percentage on indicator and had a flashing sight glass. Leaked checked rack and found no leaks. I then leaked checked store and immediately got hits on my leak detector as soon as i went inside; indicating a big leak. After spending time leak checking I finally located leak at the cat walk of walk in cooler on sys B4. Leak was at the suction pipe. Made repair and leaked checked. No more other leaks found. Picked up 480 lbs of 404a. Rack only took 288lbs of 404a. Will return extra refrigerant. Rack is now at 30% receiver level. notified manager about all findings and CALL IS COMPLETE. | Compressors/Motors | Compressors/Motors | 0.99855
Time in 0945 time out 1300 Arrived on-site checked in with manager Blanca. Went to receiving. Found the end cap for the return duct work going to receiving. Went to Home Depot and got some flat metal and built a new end cap for ductwork. Call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99676
8/9/2023. David Rivera checked inn found the fans guards that needs changing got parts number and went to united to pick up guards came back and installed new blue fan guards. Job is complete. PO#64788 | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99669
Arrived on site and checked in with manager Gained roof access, located pharmacy RTU 23, phone system off with high head pressure alarm on the controller, reset system and tested operation, everything came back on, supply temp 51 degrees and zone temperature of 73 degrees on departure Inspected electrical and tested pressure, everything is operating properly at this time, but I did notice that the condenser coil is dirty in need of a wash down and the filters haven’t been changed since July of last year, that service is covered by a separate company Call complete checked out with manager Aaron and notified him on the cleaning of the coil and filters | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99732
Andrew Debeaulieau 8/8/23 Travel 0530 Arrival 0700 Departure 1100 Breaker for compressor 4 on rack A tripped. Checked and found no shorts. Found burn wire on top of contactor. Clipped burnt section and reland wires on contactor. Restarted compressor. Found 108-115v drop across contact points on middle phase. Replaced contactor and auxiliary switch. Compressor back online. Call complete. | Compressors/Motors | Compressors/Motors | 0.99861
Arrived to site checked in with mod tony On-site to replace compressor on Cafe WIC Recieved access to rooftop Recovered refrigerant charge and removed old compressor Installed new compressor and re piped lines do to lines not meeting the same as old compressor Compressor brazed in, new drier installed, new contactor and new start components Pulled 30 min vaccum Down to 500 microns and holding Opened up valves to break vaccum Added 3lbs of R404A to clear sight glass Checked all ops Compressor LPS and HPS tested and verified they are opening as set to Refrigerant flavor: R404A Pressures: Hi 300lbs low 50lbs Removed all equipment off roof and closed up unit Cooler down to sp temp of 38F and holding Verified all fans are running Cooler at temp, no alarms Checked out with mod tony Job complete | Compressors/Motors | Compressors/Motors | 0.99855
8/18/2023 9:42:12 AM Smith, Stephen -0001 EnRoute: 8:00 Time In: 9:00 Time Out:11:15 Ticket was a duplicate ticket due to the emergency call this AM | Nuisance Calls | Nuisance Calls | 0.99826
En Route: 1630 Time In: 1745 Time Out: 1945 Comp B-2 L/O (Home Office Alarm) Gained access to Rack B. Comp 2 was online at arrival. Rack pressures @ 50/258. Outdoor ambient between 105-110 and could have caused the condenser to spike high side pressure, causing comp to temporarily lockout. Monitored compressor for awhile. No further issues found. Job Complete | Compressors/Motors | Compressors/Motors | 0.99867
Arrived at location checked door and found that door material was all tangled up had to manually adjust door to straighten out material after straightening out had to re adjust emergency exit strap after re adjusting system was alarming for unknown position tried to re position door but door would only close and would not open indicating that ac drive was damaged possibly due to a power surge at store manufacture was closed as this was diagnosed will be calling in the morning to have new ac drive NDA if in stock will update work order after I contact manufacturer | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99642
8/16/2023 2:35:04 PM Rosario, Raymond -0001 Was already on site and went over to case CS12A, where you can hear the fans tapping water. -I first removed the product from the bottom shelving to access the coil -found the condensate drain line plugged -went to the floor sink, removed paneling, removed debris clogging the floor sink -blew the clogged drain line out with C02 -once all water was drained, I cleaned up all slime and debris from the case, rinsed out with water, and removed debris from the floor drain -placed all parts back together, checked all ops, and the case is now cleaned and properly draining -this call is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
7/26/2023 7:01:13 PM Stuart, Christopher -0001 En Route: 1730 Time In: 1815 Time Out: 2015 CPU Freezer Running Warm Checked into Service Channel Checked in w/MOD Katrina Kysor Warren (CPU Freezer) M# FX5SL-03RUN S# C17H00393 R-404a Located CPU freezer. Case controller displaying an ER 7 alarm and case temp at 59. Removed deck pans and the fans were not running. Slight ice build up on distribution, suction line and in the middle of the coil. Put unit into manual defrost and de-iced coil with hot water. Put case back together and terminated defrost. Case temp got down to -2 after about an hour. Set point is -6. CPU freezer is right next to two exit doors, and constant opening and closing the doors let’s large amount of warm air into the case and ices up the coil. Checked out w/MOD Katrina Checked out of Service Channel Job Complete 7/27/2023 6:20:11 AM Smith, Stephen -0002 EnRoute: 17:30 Time In: 18:15 Time out: Assisted lead tech | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99867
7/20/23 TH TT: 8:00-9:00 Time in: 9:00 Time out:13:30 Air Curtain: Receiving Room Berner Product no: EJ866 Checked in with Service channel and MOD(Justin). Checked the location. Found the breaker on the unit was turned off. Turned it back on and found bad Door sensor and unit hunting for turn on and turn off. Talked with MOD (Justin). He needed to put the manual switch for turn on and off for this unit and needed to be cancel the Door sensor. Went to the Home Depot for pickup parts and went back to the store. Installed manual switch and ran the conduit and Electrical wire for this unit. Checked operation it with MOD (Justin). It’s working good. Cleaned work area. Informed and checked out with MOD (Justin) and Service channel. Job Finished | Nuisance Calls | Nuisance Calls | 0.99815
8/18/23 TH TT: 22:00-23:15 Time in: 23:15 Time out: 00:30 FC1-1: Grab and Go CSC Worldwide MN: C3NBRSS48-S4P SN: 205829 Checked in with Service channel and MOD (Kurt). Checked the location. Case temp showed 46 degrees F and not strong Airflow. Take the product out and Evap Coil is clean and no iced. Found Honey combs and Condenser Coil were dirty and Cleaned them. Verify temperature sensor with water iced and Found bad temperature sensor. Picked up new temperature sensor in my truck stock. Replaced the new temperature sensor and verified it with water iced. It’s read correct temp. Checked the Compressor cut in at 40 Degree F and cut out at 36 Degree F. Checked the Temperature at case showed between 37 to 40 Degrees F. Cleaned work area. Informed and checked out with MOD (Kurt) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
8/1/23 Ray Gary Arrived onsite and checked in with the manager (Rae) I found the door hinge busted in half Because of the hazard the freezer cannot be used I tryed to see if I could get a temporary fix It worked but I was unsure of it so I removed it I didn’t want an employee getting Hurt I sent Mr Reyes all the information needed to get the hinge I’m seeking it to be expedited THIS JOB IS ON PARTS HOLD | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99629
found a wire short near light toggle switch and also in an abandoned electrical whip. we went through wiring and got rid of the electrical whip that was arcing out. we then labeled the breakers with the appropriate case systems and labeled them fans and lights. we then put case back together and got all case and shelves lights on. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.997
8/21/2023 5:31:45 PM St. Amant, Kenneth -0001 Sam Club #: 6624 System: A07/A06a SC: 230819-0244 PO: 254177116 —————— 8/21/23 Kenneth St.Amant Checked in with manager Arrived on site checked in with location gained access. Bakery freezer coil was a little frost on them so I put into defrost and I all the frost is gone The defrost terminate temperature was set to high at 70 so call home office and had them change the defrost terminate temperature to 55 Bakery freezer back at temperature The gate to get in the motor room had no lock or chain so when to Home Depot for a new lock and chain A06a took case apart and it was really ice up in the back of the coil There was trash and there was a trash in the back of the coil blocking the water to it ice up due for the trash blocking the water Put case back together and it at temperature Checked out with manager Markeith Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99849
7/14/2023 12:33:30 PM Johnston, Andrew -0001 Checked in with manager and was told the damage was repaired by the plumbing company’s electrician. Verified the systems were running well then checked out with manager, call complete. | Damage by Customer | Damage by Customer | 0.97474
Start time-1400 End time-1945 complete check in with manager Ruben MTB23 A,B, and C coils and iced up put coils in defrost and de-iced coils cleaned up ice and water on the ground call is related to #248675516 checked out with manager Sammy Wonn | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99854
0630-0730 travel OT 0730-0830 labor OT Arrived on site and checked in with manager Jeffrey Located system MTB-S9.2 Upon arrival found fan casings full of water throughout the entire case Water was not allowing proper airflow thru the coils and temp was taking longer than normal to drop after defrost periods and causing ice build up Removed water from casings Little ice build up melted during defrost System should run normally now Checked out with manager Jeffrey | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99831
Meat Cooler MTB-15 Rail Damaged Time in 1500 Time out 1800 7/21/2023 Robert F & Bill L Already onsite and checked into ivr and with mod. Meat cooler bottom guide rail is damaged and coming off. Removed screws and removed bottom guide rail. Then used grinder to remove broken screws in door. Used drill bit to pre drill holes in stainless steel to mount new bottom guide rail off of truck stock. Used new self drilling screws to attach new bottom guide rail to door. Found top of bent out and not sealing. Used ladder and adjusted door for best operations and closed gap in door. Checked door operations several times and door is working properly now. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99688
checked on Cafe freezer walk in while onsitefor another call. Cafe freezer is at 0 degrees. All operations check out. this call is now complete. | Nuisance Calls | Nuisance Calls | 0.99825
SC 6609 System: MTC-9B WO#: 230812-0119 SC: 253594304 —————— Date: 8/14/23 Travel: 0600-0715 On Site: 0715-1200 Arrived at store. Checked in with manager. Manager said that the water treatment company was working on the water tower. Found cooler had coils icing up inside. Waited for water treatment to leave. Got access to scissor lift. Found MTC-9 running at 50psi suction R404a. (15°SST) Got on top of box and adjusted EPR and set to 62psi. (25°SST) Verified cooler was no longer icing up and temps were at set point. Cooler is no longer leaking water. Found no other issues. Checked out with manager. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99813
Start time-0800 End time-0930 checked in with manager Al Obregon moved meat products from case MTB-02B MTB-02a MTB-02a running at temp 28.5 took case MTB-02b apart to de-ice turn valve off for refrigeration drain clogged up took co2 to clean it out de-ice coils, opened refrigeration valve back up put case back together, put product back case dropped to 27 degrees set point 28 checked out with manager Al Obregon | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99835
Anthony Robak Checked in with MOD Carla Went to rack house for compressor lockout found on ticket 221227-0012 Found rack running critical suction but all circuits at temp Found compressor 1 in oil lockout, 4 off on head pressure, and 5 off on amp protection, Reset comp 5 and found it pulling 75 amps on start up and maintaining 55 amps when running over time span of 5 minutes Amp draw is too high Compressor 5 is bad Pumped down compressor one and checked oil transducer screen Checked comp 1 oil screen and found it severely dirty Cleaned screen Comp 1 maintains good oil pressure Checked contactor and found it severely pitted Changed contactor with DP350240 Comp 1 back online Reset compressor 4 after cleaning condenser on separate ticket Rack running at suction setpoint All circuits at temp Will order compressor 5 Model Carlyle 06ER4756SO Checked out with Ryan parts on order | Compressors/Motors | Compressors/Motors | 0.99853
Travel to: 0730-0800 Labor: 0800-1030 Replaced both broken alarms in Bakery. A09 and B28. Job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99659
8/3 Checked in with manager. High temperatures at casing was caused from issues at the rack Found that all the compressors were locked out on oil failure due to low oil levels. Added 1 gallon of oil to rack and made sure oil level was above the first sight glass in the reservoir. Reset controller and got the rack back on. All compressors ended up tripping on high discharge due to dirty condenser. Cleaned condensers and was able to lower discharge pressure and got compressors 2,3,&4 back up and running Compressor 1 is down and is having internal mechanical issues. Got with Jim Mortel and he instructed me to isolate the compressor and he will follow up to further diagnose. All circuits are back down to set-points and pressures and temperatures at the rack are within proper ranges . The repairs were made on work order 230802-0231. Followed up on 8/3 to make sure circuit is reaching set-point temperature. | Compressors/Motors | Compressors/Motors | 0.99853
8/17/2023 11:34:56 AM Stuart, Christopher -0001 Time In: 1245 Time Out: 1300 LTA 02 POS High Temping Graphed out LT 02’s temps, and it reaches -2 4 on a consistent basis. POS only gets down to temp when the other POS freezer has a circuit in defrost. Liquid receiver is only reading 15% and there is not enough refrigerant available for all circuits to maintain set point temps. All fans are operational and coils are not iced up. Will leak search and add refrigerant on different W.O. (253032801) Job Complete | Compressors/Motors | Compressors/Motors | 0.99639
8/8/2023 7:57:12 AM Gary, Raymond -0001 8/8/23 Arrived onsite and checked in with the manager (Mario) I found this case not refrigerating So I went thru and checked fans The coil to see if it was iced over All looked good So I went to the Rackroom and checked compressors any alarms I checked the circuit and I found that the liquid line ball valve was closed I open the valve and checked the case I let it temp out and told Mario the case is good to go They have construction going on here so they might have turned it off by accident THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99807
8/27/2023 8:40:58 PM Carrasco, Ethan -0001 Arrived to store for all rack repairs. Replaced all parts that were ordered on quote and verified rack operation. While on site assisted in completion of rack B compressor swap. No further issues found at this time. 8/28/2023 9:38:52 AM Giron, Joshua -0002 8/25/2023 Assisted worker | Compressors/Motors | Compressors/Motors | 0.99853
8/14/2023 12:01:11 PM Barajas, Marc -0001 SC 6609 System: MTC-9B WO#: 230812-0119 SC: 253594304 —————— Date: 8/14/23 Arrived at store. Checked in with manager. Manager said that the water treatment company was working on the water tower. Found cooler had coils icing up inside. Waited for water treatment to leave. Got access to scissor lift. Found MTC-9 running at 50psi suction R404a. (15°SST) Got on top of box and adjusted EPR and set to 62psi. (25°SST) Verified cooler was no longer icing up and temps were at set point. Cooler is no longer leaking water. Found no other issues. Checked out with manager. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99806
8/7/ Hall, Warren -0002 8/7/23 arrived on site and checked in with MOD. Went to case and found case hot and no refrigeration present. Went to roof and found unit off on high head pressure with a manual reset. May need to replace high pressure switch. Reset unit and placed in service. Unit is back in service and temperature is dropping. 8/7/2023 Petty, Kevin -0001 Found unit tripped on high pressure switch. Reset switch and made sure unit not running high pressure. May need to replace high pressure switch Unit not running high now. | Compressors/Motors | Compressors/Motors | 0.99819
8/17/2023 4:25:58 PM Toomer, Collin -0001 ST:12:30-15:15 TT:15:15-16:30 OT TT:16:30-18:30 Arrived checked in with Jose Located the meat cooler, after getting lift noticed fan blade busted and the fan was ripped outta place, Was able to use self tapping screw to reinstall fan motor and bracket, installed new fan blade. Tested fan operations. No data tag on the evap coil to be able to get M/S it’s missing. Checked out with Jose | Compressors/Motors | Compressors/Motors | 0.99812
Arrive onsite and checked in with service channel and MOD Serked Rack B Compressor 4 -Compressor 4 offline. Troubleshoot wiring -Found compressor contactor coil connector loose -Connect and secure connector -Monitor and compressor back online. -Locate manager and talked to MOD Serked and explained what I did -Job complete. | Compressors/Motors | Compressors/Motors | 0.99866
Travel: 1900 Time in: 2000 Time out: 0030 checked in with mod Located produce walk in cooler Grabbed new produce walk in door Accessed scissor lift Removed old door Used scissor lift to hoist new door up Put in new door and chain hoist Got door functioning properly and produce walk in cooler now has door Checked out with mod Call complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99679
Walk in frozen door. 07/31/2023 Dylan Lopez Travel time 05:45 Time in 08:30 Time out 17:00 Arrived on site checked in and out with manager and service channel help assist tech on what needed to be done. See lead techs notes. Call complete | Nuisance Calls | Nuisance Calls | 0.99837
Ti 0930 To 1200 2.5 regular Assisted Austin with diagnostic on the floral case. Replaced start components and cleaned condenser. Everything is working properly. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99546
7/20/2023 1:01:36 PM Rivera, David -0001 7/20/2023. David Rivera checked in found fan not working. Went to get lift took guard off and fan . Went to get parts came back and installed the fan and cleaned up . Job is completed | Compressors/Motors | Compressors/Motors | 0.99791
8/23/2023 2:31:34 PM Garreans, David -0001 Time in 1600 Time out 1630 Checked in with manager Ron. B10 M# ADT130AK S# D05L16490 Fan is not making any noises at all. Turned motors off and back on, there were no abnormal noises at all. Manager Ron said to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.99832
0730 am -14:30 pm (7 hours REG) Arrived on site with compressor and main technician Jose Cerda. Accessed roof. Took apart old compressor and sealed it off. Crane showed up and hoisted new compressor up. Installed new compressor, wired in contactor and auxiliary switch. Job is complete. | Compressors/Motors | Compressors/Motors | 0.99864
7/18/2023 Bob E and Robert On arrival tech check in with service channel and store manager. Helped Robert repair produce roll in door. See Roberts notes and pictures job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99689
Labor: 1600-1630 Travel from: 1630-1700 Checked in with MOD -David. Call was sent in unsatisfactory by mistake. Job complete. | Nuisance Calls | Nuisance Calls | 0.99833
Checked case or running at a med temp set point checked product not freezing and Monitor cases ran through defrost temps came back in range | Nuisance Calls | Nuisance Calls | 0.99827
8/2/2023 1:35:54 PM Cervantes, Carlos -0001 Travel: 0630-0830 On-site: 0830-1400 On arrival checked in with store manager and directed me to produce walk in cooler and stated one of the fans were not working. We waited for customers to finish there shopping at produce cooler. Once clear i had an employee spot to get scissor lift from receiving to produce cooler. Found that evap motor was in good condition of fan blade was damaged. Went to local supply house and picked up anew fan blade and made replacement. Installed and verified normal operation. Notified manager about findings and CALL IS COMPLETE | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99652
8/10/2023 Ceja, Mario -0001 Arrived on site checked in with manager and service channel . Located coffin case 16.1a high temping at 36 . Removed product and found evap coil completely iced up . Shut off ball valve and let coil deice itself . Found drain pan clogged and icing up coil . Cleared trash and drain line . Will return tomorrow to turn circuit back on . No further issues . Follow up 11/14/2023 Boscan, Adrian -0003 We arrived at the store, we checked with the manager, we went to the case and checked how it was running, the case is running at its regular temperature and everything is working well. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
7/20/2023 11:55:35 AM Arriaga, Luis -0001 Arrived on site checked in found coils making noise and iced up due to having the plastic wrap around the fan motors and blades stopping them and causing them to high temp I had secondary tech assist as spotter for lift and took all the plastic wraps off deiced the coils and came down to temp and no longer making any noise checked out with Norma Navarro | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99848
0730-1400 6.5 hours reg time arrived on site, checked in with Wendy, replaced Condenser fan motor and flan blade, cleaned coil that was full of grease and dirt. case is dropped in temp and functioning properly. checked out with Wendy | Compressors/Motors | Compressors/Motors | 0.99791
8/8/2023 1:04:16 PM Brooks, Byron -0001 Travel: 0830 Time in: 1130 Time out: 1300 arrived at sams club Checked in with MOD Located meat prep walk in cooler Located leak dripping from fan from condenser Accessed scissor lift Disassembled case Cleared drain pipe and drained water from drain pan Drain pan full of muck Spoke with manager to set up coil cleanings F/U Monday night to clean coils and drain pan 8/21/2023 5:29:05 AM Brooks, Byron -0002 Travel: 1115 Time in: 1200 Time out: 1700 checked in with MOD Located MTB5A+B Leak coming from fan Accessed scissor lift Turned off fans Removed insulation from drain pipe Disattached drain pan from drain pipe Used C02 and water to clear drain pipe Noticed drain pan to dirty to just use water to clean Removed entire drain pan Washed muck out of drain pan and used rags to clean Used scissor lift to housed drain pan back up and reassemble it Reconnected drain pipe to drain pan Reinsulated drain pipe Went to rack room to check defrost on unit and it was Noticed rack rack room and condesers dirty Cleaned rack room and condensers Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99795
Checked case remove coves cleaned out pan cleaned out hose to pan put back in service | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99812
7/26/2023 Bob and Glenn Bakery walk in freezer LTA-6 warehouse side door. Both sides of door gaskets are damaged and torn. Also left side end of door splitting apart. Removed all damaged door gasket and installed new gasket retainer and foam cell filler inside gaskets. Also repaired door with new angle metal. And adjusted door floor stay rollers.Check all operations all good door now working properly and sealing properly job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99724
Job completed Arrived on site for a bakery cooler freezer door, not closing correctly. I adjusted the striker where the door would close and stay closed and everything is working fine at this time. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99712
Arrive onsite and checked in with service channel and MOD Helia. Grab & Go Cafe MT RC2 -Request to removed product and Cafe lead team just want to removed one section -Install gauges and found service schrader valve is bubbling -Replaced schrader valve -Condenser sight glass is flashing hard -Leak checked case and condenser. No more leak found. Service schrader valve faulty caused loosing refrigerant. -Charge system of 6lbs 1oz of R404a -Leak check case and condenser. No more leak -Compressor amp reading is 3.82amps -Monitor case and case temp went down to 34f -Locate a manager and talked to MOD Justin and showed him the case -Job complete. | Damage by Customer | Damage by Customer | 0.98248
8/23/23 JP -Arrived on site and checked in with mod PA Went to LTA3-a to look into issues while looking at case was asked to look at the Main WIF due to shaking violently and having a loud noise. -Paused looking into case to deal with WIF -pulled case apart and found #2 fan at sensor not running and had short on pigtail looks to have been pinched by fan plenum. Repaired short and case at -9° now Cleaned up and checked out | Compressors/Motors | Compressors/Motors | 0.99806
TRAVEL TIME=0 TIME IN=0400 TIME OUT=0415 07/24/23-AARON BIGGS DUPLICATE CALL. PLEASE REFER TO WO#230717-0357 PO#251131478 JOB COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99824
7/24/2023 8:44:33 PM Stark, Keith -0001 Found all compressors on rack b running. Discharge pressure is running at 345. I shutdown the rack and condenser. I washed out the condenser coils. Head pressure is now running at 265psi. All cases are now down to temperature. 7/25/2023 6:54:02 PM Grant, Markus -0002 Found all compressors on rack b running. Discharge pressure is running at 345. I shutdown the rack and condenser. I washed out the condenser coils. Head pressure is now running at 265psi. All cases are now down to temperature. 7/31/2023 6:14:45 AM Stark, Keith -0001 Found all compressors on rack b running. Discharge pressure is running at 345. I shutdown the rack and condenser. I washed out the condenser coils. Head pressure is now running at 265psi. All cases are now down to temperature. | Compressors/Motors | Compressors/Motors | 0.9984
Got to the location and checked in with Manager POOJA SALOOJA when up to the pos cooler and found coil # 2 with an ice up drain pan. Got with Alan and he will fallow up on this call. He will be tomorrow to de-ice it. Talked to the manger to have those two plates move from the top to give him some room. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
Located self contained cooler and found compressor short cycling also noticed hard-start capacitor got disconnected on one side. So I rewired capacitor and got compressor. Temperature dropped and cleared alarm | Compressors/Motors | Compressors/Motors | 0.99862
Returned and replaced condenser fan motor . Replaced all three fuses .now up and running .. | Compressors/Motors | Compressors/Motors | 0.99742
7/25/2023 12:30:19 PM Warden, Cody -0001 Responding to unit not “blowing” in fuel hut. Checked in with manager/Jacob APw/ Mcclean Model cr43-08-16-051 Serial 0215508544-3 Inspected return to find there was no filter in place. Coils were badly plugged. Checked refrigerant pressures which were a little low. Verified operation of blower for correct voltage and amperage which were both good. Cleaned condenser coils and the evaporator coils to ensure proper airflow to efficiently cool and condense refrigerant. Checked out with manager/ Lamont Turner 7/26/2023 6:41:59 PM Decarlo, Anthony -0002 Awp proair M#CR43-0616-051 S#021550844-3 Checked in with mod and service channel on arrival Went to gas station hut A/c unit. Found breaker off at panel. Verified return coil has extensive fin damage causing restriction. Switched on, unit is running but not blowing cool air Opened up a/c panel verified comp receiving power. Checked starting components and caps are well within spec Checked safeties, all are closed. Checked Tstat, verified closed calling for cool Checked windings found within spec Power cycled unit multiple times, hearing a clicking coming within compressor. Verified comp is over amping over 40amp and cutting out power. Internal overload is too weak Unit it’s out dated with r22 charge. Quote to replace old unit with 120v ductless mini split unit. Call incomplete Checked out with mod analisia and service channel on departure Bill for incurred | Capital Replacement | Capital Replacement | 0.97668
9/13/2023 5:19:19 PM Barajas, Armando -0002 Assisted tech with temporary repairs to drain pan. 9/27/2023 6:18:05 AM Ried, Nicholas -0003 Completed. Checked in with management. Spoke with employees in Home Meal solutions. Waited for food prep to be completed and all food removed from the area. Removed old drain pan. Installed new pan. Installed fan guards and temp sensor. Cleaned unit. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99691
on-site 2430-0230 Arrived on site. Made way to RackA. Found comp3 & comp1 not running Comp3 was not calling, comp1 was tripped on oil lock out Reset oil control for comp1, compressor is running and operating properly Checked gas and oil pressure, checks ok Checked pressure drop across filters, checks ok. Comp3 cycled on when calling to run All checks okay at this time Job complete | Compressors/Motors | Compressors/Motors | 0.99833
7/25/2023 10:39:00 PM Ruiz-Serafin, Alex -0001 MTB compressor 4 lockout -Arrived onsite checked in with MOD Todd received motor room access located rack b and found compressor off on oil pressure reset OFC checked NOP monitored compressor did a capacity check on compressor all checks out good informed MOD of job performed and checked out | Compressors/Motors | Compressors/Motors | 0.99858
8/7/2023 3:17:09 PM Upchurch, Keith -0001 Time in 0945 time out 1300 Arrived on-site checked in with manager Blanca. Went to receiving. Found the end cap for the return duct work going to receiving. Went to Home Depot and got some flat metal and built a new end cap for ductwork. Call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99693
On site. Labor: 1100-1630 Diagnosed grounded exhaust motor and a defective TStat. TStat was sending 120V but could not sustain the load. Belt was also broken. Picked up parts and material. Replaced motor and belt. Set tension. Spliced wire in 1-gang box and ran conduit to new TStat. Tested all components. Motor pulling 5.2A/7.4A. Rotation normal. Thermostat set to 80°f per David. Job complete. | Compressors/Motors | Compressors/Motors | 0.998
Travel OT: 16:30-17:00 Onsite OT: 17:00-19:30 Sn# Sam’s Club 6610 Sc# 230814-0586 Po# 253718583 System: CS 8.4 Upon arrival checked in with MOD and ServiceChannel -Located case CS 8.4 -Actual case temperature within normal range -Verified proper sensor functioning by using ice bath -Sensor responding normally -Sensor covered in dust and debris -Cleaned sensor -Located dual temp switches in electrical room -DTC for CS 8.4 had been switched from normal temp to energy saving temp -Switched back to Normal temp -Verified case was at temp before departure -Informed MOD of work performed and obtained a signature before my departure. Job complete | Nuisance Calls | Nuisance Calls | 0.99807
SINGLE CASE TEMP Rack Associated: MTC System 7/26/2023 2:35:11 PM Calderon, Jose -0001 Checked in with manager tiger and inspected case MTC 19 and it was at temp from the previous body they had de-iced the case and it is now running at temp 30F. Inspected cooler and saw it was iced up and set it to a defrost and de-iced the coils. Coil is now de-iced and running at temp. The coils iced up because of intermittent power failures caused the rack to go down and the controllers to glitch and while refrigeration was valves on the fans were not running and it cause incomplete defrosts. The rack was brought back up, but the controllers were glitched. Reset the controllers and after the defrosts the cases and the produce cooler got back down to temp. KRACK MODEL # GND56A-340TDB-STP WT ST ST ST SERIAL # MY21C020840 Let the manager know that the produce cooler was at temp and running normally and that the controllers are running normally. Let the manager know to have an electrician inspect the health of the electrical power coming in to the store as intermittent power failures are common at this store. Checked out with manager silva Call Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
Completed Checked in with manger on site went to lta 2 freezer adjusted door and fixing wiring for heaters then cleaned up and hualed old door off and pallet box it was in no other issue ncomplete Checked in with manger on site went to LTA -2 freezer replaced sliding door and door track eith all brand new hardware no other issue found will return tomorrow morning to pick up old door | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99558
8/28/2023 5:48:46 PM Maldonado, Chris -0001 Start time-1730 End time-1900 checked in with manager Demora lyons checked case MT-SC3 MD PIZZA MT-SC5, case at temp called home office to confirm temp they said no alarms and it’s reading temp checked out with manager Demora lyons | Nuisance Calls | Nuisance Calls | 0.99812
Jul 18, 2023 I opened up an extra discharge line and replaced discharge control on comp 2, all ok. | Compressors/Motors | Compressors/Motors | 0.97637
EnRoute: 18:30 Time In: 19:15 Time Out: 20:45 Arrived and checked in with the manager. Rack B was down upon arrival due to a compressor change out. Was not able to properly diagnose issue. Need to return once rack is back up and running. Will need a follow up call. | Compressors/Motors | Compressors/Motors | 0.98183
8/15/2023 2:14:57 PM Garreans, David -0001 Time in 1000 Time out 1630 Checked in with manager Maricsa. Racks A M# TC500-085-SL-4-NVF-A S# 0202001182 Tg# 0054076 The sprinkler was turned off in attempt to see if rack could run with out it and pressure increased to over 335 psi, even with all condenser fan motors running and coil is clean. I tried to pump rack down to change drier cores, the valves on one side of shell is not holding. I had to move gas to rack B to temporarily isolate the receiver and drier core shell together in order to change cores. Got everything back up and running and verified operation. Will leave sprinkler on. Checked out with manager Jonathan. Complete | Compressors/Motors | Compressors/Motors | 0.9955
Was already on site CT board was replaced on other work order 230811–0056. Service channel 253489054 Temperature at case AS05 and AS06 is now maintaining proper temperature made adjustments to controller. Continue to monitor ensure case temperature maintains average of 35F. Satellite compressor 3 has not tripped for alarm after replacing CT board this call is now completed cases are both reaching set point | Compressors/Motors | Compressors/Motors | 0.99752
Jul 17, 2023 Dairy WI coil is slightly iced up. Will need to return to deice and diagnose issues. De-iced C18 dairy WI box coil. Checked and adjusted SH, confirmed valve screens are clean. SH was at 2°, raised it to 10°, confirmed defrost operation. System is operating OK. Put evaporator back together and cleaned up cooler/work area. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99859
7/28/2023 3:19:28 PM Hanamornsate, Thirathanawat -0001 7/28/23 TH Time in: 14:30 Time out: 15:00 Refrigerator (Break Room) True MN: T-23-HC SN: 10529373 Arrived on site and checked in with Service channel and MOD(Hilda). This called is duplicated call. Reference PO# 250963827. Informed and checked out with MOD(Hilda) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99842
Jul 20, 2023 Found compressor not operating with power supply on floral case. Found start components bad. Replaced with new, now up and running. Need to contact manufacturer to find out about correct drain pan size, will order new for case. Let store know given condition of compressor, start components are bad and compressor might go out soon. Jul 24, 2023 Drain pan getting completed under 15th work order. | Compressors/Motors | Compressors/Motors | 0.98135
Aug 15, 2023 Found BS suction pressure at 85 psi. Comp 2 and 3 on the BS suction group had no oil. Reservoir had 2 balls floating. I found plugged up oil filter and the oil feed line to all compressors smashed. Changed out oil filter, pumped out oil feed line, and replaced the damaged oil line. I got oil to feed back to all the compressors. Comp 2 on BS group was still going off on oil. Found a control wire had come off coil of contactor. I repaired spade and re secured to coil of contactor. Found the T1 and T3 wires from contactor to compressor only secured to contactor lugs by a single strand of copper. I repaired the wires and resecured back to contactor. All compressors back online. The company that is doing the rack refurbishing is replacing all the compressor controls for this rack. | Compressors/Motors | Compressors/Motors | 0.99857
07/21/23 Noe Lopez Travel: 0800 Arrival: 0930 Departure:1830 System: Cafe HVAC RTU 13 -Checked in with MOD -Manager stated cafe is running warm -Went to check controller everything came out good -Called digital assets and verified everything was fine on there end -Went to unit to inspect it -Filter was fine -Cleaned out evaporator had some gunk on it -Condenser coil looked very dirty -No water outlet available -Went to Home Depot to pick up 200ft of water hose (left hoses in room on roof) -Used numerous cycles of water to rinse coils off, large amount of dust and dirt came off -Cleaned out other condenser coils that were next to RTU 13 -Cleaned of drain line as well -Put unit back together -Checked controller everything checked out fine -Upon reviewing the cafe area noticed the heat was coming from pizza oven -Went to inspect exhaust fast, motor was spinning slow -Turned breaker off and on unit was not functioning -Determined motor will have to be replace -Manager put ticket in 251531230 -Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
8/20/2023 11:27:19 AM Delgado, Jesus -0001 Check in with manager Mike, on arrival was shown endcap was told case B 11 had poor flow Notice display case, showing clean mode. Reset, controller under case with no change cycle through parameters manually force from clean mode to refrigeration. Chase is now displaying temperature and is refrigerating. waited for case to reach setpoint of 30f. case now has airflow all at normal at this time Explain to management this call is completed | Nuisance Calls | Nuisance Calls | 0.9946
7/25/2023 Romero, Gabriel -0001 TPP-AT-67-HC 10150628 -Arrived on site and checked into service channel and with MOD. -Located pizza prep table in food court. -Found outlet to case with a tear on wire exposing inner wires, some copper wire exposed, suspect wire was dragged across floor. -Too much slack on outlet wire causing it to be dragged around. -Covered exposed wire with vinyl tape and secured loose outlet wire to case with zip ties to prevent further damage. -All system ops ok at this time. -Job complete. | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.99653
7/31/2023 7:23:26 PM Garreans, David -0001 TTOT 1800-1900 Time in 1900 Time out 2130 Checked in with manager Payne. Rack A M# RNSX-D8-L064-M045-V4XLA-A S# S16H00036 TG# 0050160 The entire rack A / AS was down. All compressors locked out and overheating. I valved off every compressor and started 1 compressor up at a time. All compressors have oil, are running and holding good suction pressure. Discharge pressure with all compressors calling is at 260 psi. All circuits out of alarm. Checked out with manager Payne. Complete | Compressors/Motors | Compressors/Motors | 0.9986
Time In: 1330 Time Out: 1430 B1.1 MD Produce Hi Temp (Home Office Call) Case temp at 37 on arrival, with a set point of 31. Removed some product, deck pans and accessed the evap coil. The coil was slightly iced up and both fans were operational. Found oil stains below the TXV. Leak checked and the TXV screen was slightly loose. Tightened the screen and the leak was sealed. Removed small ice build up with hot water. Accessed Rack B. Sight glass solid, receiver at 25%. Checked defrost parameters, and the case has 6 defrosts with a term temp of 47. Called Home Office and had them change the defrost term priority to duration to allow case to have full defrost cycles. Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99859
7/28/2023 1:02:35 PM Emmer, Bob -0001 7/26/2023 Bob On arrival tech check in with service channel and store manager. After picking up parts. Removed all damaged door gaskets and installed new magnetic door gasket on both 3 door merchandise cases in front entrance. Adjusted 1 door to close properly. Job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99735
7/31/2023 11:45:37 AM Scheel, Jaymen -0001 Arrived on site and checked in with manager skyla. Gained access to roof and started checking for a compressor that was locked out. Didn’t find one in rack b went to rack a and started checking over the compressors. Didn’t find one tripped. Looked over compressor 1 and it was running properly and had oil in the reservoir. Checked pressure of oil pump compared to the suction pressure and suction pressure was 18psi and oil pump pressure was 60psi. Checked the oil pressure sensor by jumping out and seeing if the compressor kept running. Compressor ran fine with it jumped out. No issues found on compressor. Call complete checked out with manager Victoria | Compressors/Motors | Compressors/Motors | 0.99858
8/9/2023 Rodriguez, Mateo -0001 Arrived on site and checked in with manager Sandra Located bakery walk in cooler Found safety strap on the inside of door pulled and buckle was stuck on door Freed buckle and put strap back in place Using jog function on controller I put the door down. Made sure no error codes were present. Pushed open button to test. Door opened ok Tested door several times opening and closing it to make sure it functioned good Door working normally now Job complete Checked out with manager Sandra | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.94583
TRAVEL TIME=0700-0800 TIME IN=0800 TIME OUT=0830 07/19/23-AARON BIGGS-SYSTEM#C7-b PREPED MEALS CASE UPON ARRIVAL CHECKED IN WITH MOD JAIME. Call is duplicate call. Confirmed call is a duplicate. REFER WO#230719-0085 PO#251289427 JOB COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99825
Rack Associated: CLTAB Systems Affected: B4.1 MD DAIRY / DAT 3 / 63.2 °F,BS07 MD CAKE / DAT 2 / 47.8 °F Alarm Message: Multi Case Temp Manual Comment: BS07 reading 39.39 setpoint 32 B4.1 reading 42 setpoint 32 HOME OFFICE ONLY Refrigeration -HO Use Only Case -Coffin/Bunker High Temperature Raised By: Aida Mast Contact: NA Position: NA Scheduled date: July 15, 20231:36 PM 7/20/2023 5:23:26 AM Biggs, Aaron -0001 UPON ARRIVAL CHECKED IN WITH MOD JAIME Múltiple SYSTEMS SENDING GHOST ALARMS while actually being at proper temperature. Store is currently undergoing a cutover from SPECTRUM TO OPUS NETWORK. MULTIPLE SYSTEMS ARE NOW ON THE OPUS NETWORK BUT STORE STILL USING SPECTRUM NETWORK SO HOME OFFICE CANT SEE ANYTHING ON THE NEW NETWORK. Will need to get more info on who’s doing the job and when the cutover will be done. Will follow up accordingly after speaking with contractor. 7/24/2023 12:04:34 AM Jackman, Nick -0003 Arrived on site checked in with service channel and manager Found fan unplugged Sys bs07 Plugged fan in now at temps Sys B4.1 found honeycomb Blocking air flow Installed honey combs correctly case at temp Verified opus controller is able to see case Please see pictures call complete | Nuisance Calls | Nuisance Calls | 0.99729
7/27/2023 1:05:53 PM Delgado, Jesus -0001 Food court Walk-in cooler heat craft model SME054VE serial number D05L16422 Unit disconnect was off walk-in box was above 60 F product was removed. Power unit on. Compressor Short cycling found run capacitor has failed. Remove and replace with same type check start capacitor check refrigerant. pump compressor down. Verify condensing unit is working. Box is now at set point . This call is completed. Parts used 15 MFD capacitor | Compressors/Motors | Compressors/Motors | 0.99281
Duplicate call see wo 230718-0335 | Nuisance Calls | Nuisance Calls | 0.998
After finishing previous call checked rack room found all compressor running and nothing in alarm walked the store and found a end cap Case read 75 degrees had meat department pull the case to save product pulled all shelves out and the the back panels found both Evaporator coils iced up closed the liquid line hand valve and unplugged the fans deuces the coils double checked both coils free of ice build up Opened the liquid line hand valve and plugged all fan fan came on put the back panels on and bottom shelves checked for air flow Had good air flow put all shelving back in the case and watched temps fall to required set points found no other issues job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99829
Sam’s club #: 6619 System: compressor B1 SC: 230717-0612 PO: 251183533 —————— 7/18/23 Kenneth St.Amant Travel-06:00-08:00 Onsite-08:00-12:00 Checked in with manager Arrived on site checked in with location gained access. When to motor room and B1 was locked out on oil Checked oil level, oil psi and normal operating Everything is all good Compressor back online and running Checked out with manager Kelly Job complete | Compressors/Motors | Compressors/Motors | 0.99859
8/1/2023 11:06:08 AM Arriaga, Luis -0001 Arrived on site went to back found manager JT and asked about line he said its been leaking smelled like gas line they valved off the heaters I stated to manager if the gas line is leaking it would be the plumber not us and he stated then why was I there if I couldn’t fix it stated to customer they put HVAC as the source customer got angry grabbed my things as we the technicians are there to try to fix the issues not get yelled at by customer when they couldn’t put the wo in correctly 8/1/2023 9:25:13 PM Boscan, Adrian -0002 It arrived at the store, they said that it smelled like gas in the reciving part, all the heaters and gas lines with bubbles were checked in the place and one of the heaters were found on, all the valves were closed and the heaters were turned off, the place does not smell of gas and we left everything in perfect condition | Nuisance Calls | Damage by Customer | 0.90504
7/20/2023 2:05:52 PM Fuentes, Miguel -0001 11:00-16:00 labor Met with mod and discussed issues that pertained to the exhaust fan in the automotive center. The employee working in the shop told me that the store had experienced a recent power outage/surge and the breaker was found tripped off the following morning. He added that they flipped the breaker back to ON position and had attempted to toggle the ON button for the fan but no response. I got the same results. I proceeded to check for power at the toggle ON/OFF box. I found that 430-440v was present and traveling to the fan motor when the ON button is depressed. I next travelled to the roof and removed all covers up until the electrical compartment at the motor. I checked for power at the motor and found 430-440v present at the non-running motor. The motor is bad, and I need to replace it. Power is now removed for safety. After picking up a new motor at Barsco and X2 V belts, I installed the new motor along with new fan belts onto the exhaust vent. After installation was complete, I restored power to the exhaust fan to test operations. Test was good. Normal operation at this time. Job completed | Compressors/Motors | Compressors/Motors | 0.99804
Travel Time 830 Time in 1000 Time out 1130 Arrived on site checked in mod CHRIS and service channel. Proceeded to rack C. On arrival found all compressors on line and 1 was running not off on oil. No alarms on opus. Checked amps compressors amps good. Called sams club home office spoke with IDIA and also said she sees no alarms form rack C for compressor off on oil. Looks like false alarm everything up and running . Checked out mod CHRIS and service channel. JOB COMPLETE. | Compressors/Motors | Nuisance Calls | 0.99809
On-site 0915-1445 Arrived on site. Checked in with manager. Found rack in comm loss causing evaps to not run through defrost Several evap coils are completely frozen Compressors are also freezing up Receiver level at 0 Reset controller to get comms online Once online called home office to cycle evap coils into defrost Ensured defrost is operational on cases/evaps After running through defrost all ice is thawed out, no longer any ice build up on compressors Monitored to ensure temps drop within range Receiver level is currently at 55 All checks okay at this time Job complete | Compressors/Motors | Case Cleaning/Deicing | 0.99632
Sams 6685 Provo 7-31-23 Service call Po 252303773 Freezer door wont close Job complete TT/OT 2000-2100 OT 2100-2200 Found door bent and will only close half way Door gets caught on frame Hinge lifters stuck Opened door 100% and placed lifters in socket All 4 hinges bent Remove 2 bottom hinges Used door to tweak back top 2 hinges Used forklift to run over hinges to flatten back out. Re installed bottom 2 hinges with door in proper location Door now closes Door is bent couple places arent sealed Door frame separating from cooler wall Ask MOD Gatlin if I should quote new door He decided that I should complete call and let club manager make The decision. If door is wanted a new PO will be submitted. Checked out with MOD GATLIN | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99682
7/25/2023 Bob E and Glenn Tech already on site check in with service channel. Helped Glenn replace condensation pan on top of self contained case. Also found dirty evaporator coils on case and on adjacent case brushed and clean coils and use coil cleaner on both evaporator coils are both cases. Also cleaned and dried up all water on top of the case and floor. See Glenn’s notes and pictures job complete. | Misc. Billable Repairs and Service Calls | Case Cleaning/Deicing | 0.99812
7/28/23 TH TT: 8:00-9:30 Time in: 9:30 Time out: 14:00 Refrigerator (Break Room) True MN: T-23-HC SN: 10529373 Checked in with Service channel and MOD. Checked the location. Found the iced up the Coil. Plugged out the power plug. Take the Fan plenum out. Used bucket contain hot water and Deiced Coil. Dry inside the refrigerator. Put the Fan plenum and Drain pan back. Plugged in the power plug. Door gasket is good. Checked the temperature. It’s showed 37 degrees F. Informed and checked out with MOD and Service channel Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
Found compressor 3 tripped on oil . Found that unit working correctly and found no issue . Net oil pressure good as well as compressor cycled several times .if problem lpersists might need to replace compressor oil control . | Compressors/Motors | Compressors/Motors | 0.99865
7/27/2023 9:31:19 PM Paz, Christian -0001 Rack C compressor 2 and 3 alarm comp L/O . Compressors off on oil. Compressor oil levels ok. Reset oil controll. Both compressors operating ok 19amps each. Contacters ok. Check OLC k1, inspect clean glass. Tighten both oil controls. Rack oil level, oil filters ok. Cases at temperature. | Compressors/Motors | Compressors/Motors | 0.99865
John DiCecco 8-7-23 Travel 0645 Arrive 0745 Depart 0830 Checkin Checkout RTU 3 LCB060HN2G 5602E02629 Asset #003881 Arrived and inspected compressor health. Found pressures favorable and amp draw within range. Call complete. | Compressors/Motors | Compressors/Motors | 0.99505
traveled to store. found comp 1 for B rack off on a fault. the flood back is still gone from rack after adjusting txvs yesterday. I condemned compressor and valved off. I got compressor info and will get a new compressor ordered. rack still at suction pressure setpoint. | Compressors/Motors | Compressors/Motors | 0.99856
8/8/2023 8:58:32 PM Jennings, Jeromy -0001 Job incomplete Arrived on site for an alarm in the dairy cooler blew out the evaporator coil’s. Check the liquid levels on rack a hooked up my gauges to the filter dryer. Found a five psi difference. Need to have rack a filter dryer pull down and dryer’s. Replaced 8/16/2023 11:44:40 AM Paz, Christian -0002 Zone 1 leak alarm, strobe and horn alarm. Leak check walk in box with dtek stratus. Reset alarm at leak detection panel. Check zone 1 status reading 0 ppm. Alarm clear ok. Front light hanging from box. Repair light Complete | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.9025
Arrived on site checked in found coils making noise and iced up due to having the plastic wrap around the fan motors and blades stopping them and causing them to high temp I had secondary tech assist as spotter for lift and took all the plastic wraps off deiced the coils and came down to temp and no longer making any noise checked out with Norma Navarro | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99827
wIF 1.1-1.2 checked in with MOD Located WIF found evap 1.2 leaking water drain pan was hit with forklift bending the right side corner to pitch down causing water to drain from corner of the evaporator drain pan Got water melted ice from corner pushed drain pan up to level stoped leaking water down Found no other issues Job complete | Damage by Customer | Case Cleaning/Deicing | 0.99808
8/1/23 TH Time in: 17:00 Time out: 20:00 C11a: Produce CLR Heatcraft MN: WKE340BEC SN: T17D13991 C12a: Heatcraft MN: WKE340BEC SN: T17D13993 Arrived on site and checked in with Service channel and MOD (Josh). Checked the location and Found water condensate started dripping to the floor from both units. Found both Coils were very dirty. Turned off the Fan switch and take all Fan Guards and all Fan blades out and cleaned them. Cleaned the coils by brush and keep all dirt out from the drain pans. Put all Fan blades and all Fan Guards back. Cleaned drain pan by water and flushed drain pipes by CO2. No more water dripping. Cleaned work area. Informed and checked out with MOD(Josh) and Service channel. Job Finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
In 15:00 out 18:00 Gp#230808-0373 Checked in with manager amber Working on broken glass door replacement Located new door and uncredited Removed old and installed new door Adjusted door and installed all trim and other brackets Also adjusted door Door closing properly No other issues at this time job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99703
7/18/2023 4:38:42 PM Bustillos, Andrew -0001 -Was already onsite on another call manager wanted me to look at produce walk in. -Produce walk in had ice starting to build up on evaporator C9b -MOD wanted me to remove ice build up before it got worse and leaks -Removed all ice on coil using hot water -made sure no other evaporators in walk in didn’t have ice build up. -made sure drains on walk in were clear as well -all ice build up removed -made sure all fans were running properly -call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
7/14/2023 6:35:06 PM Tobe, Jeffery -0001 Upon arrival located manager to start Job went to case case was running warm went to motor room to check Novar case was in defrost watch case come out of defrost pull down the temperature all OK at this time complete | Nuisance Calls | Nuisance Calls | 0.99729
7/17/2023 6:26:03 PM CERDA, JOSE -0001 Sams 6683 Murray 1-17-23 Wo 230716-0279 Po 251007054 Compressor B2 Waiting Quote Travel 1745-1800 On job 1800-1930 Travel 1930-2000 Compressor Needed Carlyle Model 06CY665E-103 Serial 1321UE3571 Contactor needed Dp360240F Auxiliary Needed 1950243 3 gal mineral oil 200 Viscosity Needed Found compressor 1 tripped disconnect Found compressor 2 disconnect in off position Checked winding ok Checked short to ground non Found 460 at Contactor but L3 drawing 0amps Compressor single phasing B2 Shut off B2 at disconnect Left note for next tech Left B1 running amps ok Need to replace compressor B2 8/1/2023 10:53:06 AM SCHUPBACH, DUSTIN -0006 We received the wrong compressor for this call. We took compressor back and ordered the new compressor. New compressor is six weeks out. Will return to install when new compressor comes in. 8/1/2023 11:04:26 AM SMITH, ANTHONY -0004 07:30-11:00 (3.5 hours REG) Arrived on site got everything set up for compressor swap, on Rack B. Found out we received the wrong compressor for this call. Took compressor back and ordered the right compressor. New compressor is 6 -8 weeks out. Will return to install when new compressor comes in. | Compressors/Motors | Compressors/Motors | 0.99841
Arrived at location case b05 seems to be reading normal temperature setpoint 28 case temp 27.9 case b03 a and b are running warm with low airflow tried to run system through 2 defrosts had small effect will return in morning before store opens to de ice coils | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.96656
7/27/2023 8:06:00 PM Del Rio, Gabriel -0001 Arrived on site checked in with store manager gained access to work area cafe walk-in cooler MTC-U1 walk-in was temping at 65 upon arrival went to roof inspection condensing unit and determined that compressor was going off on high head due to condenser fan motor not working went to parts house picked up new motor and replaced it turned unit back on motor operates properly with no issues walk-in cooler came back down to temp call complete | Compressors/Motors | Compressors/Motors | 0.99829
8/14/2023 10:24:36 PM Saenz, Cory -0001 8/14/23 Cory Saenz Arrived on site checked in with manager picked up 8 60 pound drums of CO2 charged system with 480 pounds Co2 assisted one on new breaker install system back up and running. Will need to return to pick up CO2 cylinder. Temps coming down system back up and running. 8/14/2023 10:31:10 PM Magana, Juan -0002 -arrived on site. -found short on distribution block for rack 208vac power. -150amp breaker 208v breaker tripped. -breaker won’t reset now, it’s bad. -called bay power after hours and opened up store. -got the new breaker and returned to job site. -fitted and installed new breaker and electrical. -Daniel Blount is here for same issue but on a different ticket. -added eight 60 pound r744 cylinders to rack. -rack back operational and circuits pulled temp. -Daniel will keep his call open for a follow up to top of co2 levels up to 25% and order new distribution block. Bay power was not a vendor on our list of vendors when creating a mobile tech PO. Used the work order number as PO. Picture of invoice from bay power attached for breaker purchased. 8/15/2023 12:18:47 PM Saenz, Cory -0003 Took co2 cans back to airgas | Misc. Billable Repairs and Service Calls | Capital Replacement | 0.94573
Time in 1000 Time out 1630 Checked in with manager Maricsa. Racks A M# TC500-085-SL-4-NVF-A S# 0202001182 Tg# 0054076 The sprinkler was turned off in attempt to see if rack could run with out it and pressure increased to over 335 psi, even with all condenser fan motors running and coil is clean. I tried to pump rack down to change drier cores, the valves on one side of shell is not holding. I had to move gas to rack B to temporarily isolate the receiver and drier core shell together in order to change cores. Got everything back up and running and verified operation. Will leave sprinkler on. Checked out with manager Jonathan. Complete | Compressors/Motors | Compressors/Motors | 0.99745
Arrived on site checked in with store manager MT8 walk-in dairy box door has damage to it door was damaged from remolding construction crew who installed it manger said that he’s going to find out if the initial installed company is going to re install new door call complete | Damage by Customer | Damage by Customer | 0.98628
7/25/2023 5:21:33 PM Arriaga, Luis -0001 Arrived on site checked in went to find door door looked like it got hit cause all the bolts were moved from their place looked at brackets but everything was in tact took the door off and aligned brackets to the main door then adjusted height once we got the door to align we aligned the bumper guards at the bottom for rail to glide smooth tightened everything up and tested door working properly checked out Angel Juarez | Non-Mechanical Door Repairs | Damage by Customer | 0.98399
7/26/2023 7:09:37 PM Floyd, Jimmy -0001 Arrived onsite checked in with mod gained access to rack house checked the vfd not showing fault on b/bs rack checked compressors and idcm no issue found checked all condenser fan motors and amped motors checked the transducer for discharge I believe it’s a program issue will follow up 8/23/2023 2:45:13 PM Floyd, Jimmy -0002 Arrived onsite checked the vfd for any faults pulled graphs found the sub cooler not working and the sporlan controller frozen reset power to control and reprogrammed the controller checked operation and sub cooler everything’s working properly Call completed TECHNICIAN FIXED VALID ISSUE. VFD STARTED WORKING AFTER ISSUE WAS RESOLVED | Compressors/Motors | Compressors/Motors | 0.98699
Time In: 20:30 Time Out: 20:45 All cafe coolers & freezers have been down for over a week. Main breaker panel for the RCU’s lost power at the transformer. An electrician was on site to fix the issue last week, but the issue came back the next day. Confirmed breaker panel is still missing L1 & L2. Electrician company has been called out by MOD to make repairs. Job Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99594
8/4/2023 6:49:47 PM Smith, Stephen -0001 EnRoute: 18:30 Time In: 19:15 Time Out: 20:45 Arrived and checked in with the manager. Rack B was down upon arrival due to a compressor change out. Was not able to properly diagnose issue. Need to return once rack is back up and running. Call will be completed on 230207-0113 / 236908851. This call is complete. | Compressors/Motors | Compressors/Motors | 0.96424
8/18/2023 2:41:40 PM Verduzco, Andrew -0001 Arrived checked in and out with manager Cris Service for break room running warm Upon arrival found RTU 18 indoor blower running but no compressor or condenser fan running Unit would turn on for approx 10 min or less and would turn off Unit was not satisfied when unit would shut off Checked pressures and superheat while running and pressures are ok Found the freeze control connected to suction line after the evaporator faulty reading and incorrect temp and cause the control voltage circuit to open turning off compressor and condenser Bypassed freeze control and low pressure control is still in service Unit will run perfectly fine with low and head pressure controls with out freeze control Unit is running and is satisfying Monitored for multiple cycles of zone temp satisfaction. Call is complete | Compressors/Motors | Compressors/Motors | 0.9986
Cleaned condenser and replace bad starting components | Misc. Billable Repairs and Service Calls | Compressors/Motors | 0.55475
Job complete 8/14 Arrived onsite and checked in with management. Located temp sensor in optical doctors office which is labeled as rtu 2. Went up to roof and located rtu 2. Found the condenser fans running but the indoor fan and compressor was not. Began tracing out all high voltage and control voltage. Did not have 24v to fan or compressors, unit is not calling for cooling. Called sams monitoring and found that unit was tripped on air flow switch. Reset unit and began working properly. Checked airflow switch and is working properly and airflow is good. Checked pressures and monitored unit for normal operation. Went back down to dr office and checked temperatures and are dropping with good air flow. Will come back tomorrow to follow up on unit. 8/15 Arrived onsite and checked in with management. Went up to rtu on roof and found unit off called monitoring and got no answer. Went down stairs to doctors office and checked all temperatures. Unit was actually off on temp(satisfied). Went back upstairs to roof and waited for unit to come back on and checked pressures and for normal operation. Unit is working properly at the moment. | Nuisance Calls | Compressors/Motors | 0.99812
Travel 1730 Time in 1900 Time out 0200 Water leaking from coils and fire sprinkler in dairy cooler Arrived on site Checked in with MOD Reported that light was out in dairy cooler Couldn’t open cooler until 2015 once all customers were out the store to work in Had to work with no light whole time Accessed scissor lift Reported that a few coils were dripping water on floor Fire Sprinkler as well leaking Informed MOD that we can’t work on the fire sprinkler Coil MTC-6 dripping water had a sweaty drain pan as well Took off both drain pans Inside evaporator coil, fans, and drain pan were dirty Cleaned evaporator coil, fans, and drain pans on coil MTC-6 and MTC-4 Reassembled coils Quoted out MTC-1, MTC-2, MTC-3, and MTC-5 to be cleaned 2 techs 16 hours night job OT Approved by Supervisor Sam Lopez Checked out with MOD Mike FU Needed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
8/4/2023 10:38:03 PM Garreans, David -0001 TTOT 1945-2015 Time in 2015 Time out 0000 Rack C M# PS S# 120037 Tg# 0090050 Checked in with manager Francis There were no alarms all day for these curcuits on controller. There were no active alarms. All these circuits were still running at 49 degrees. The solenoid for subcooler on rack was not energizing properly. Subcooler needs to run all the time during these high ambient temperatures. Subcooler temperature sitting at 98 degrees and no alarms on subcooler controller. Opus operates the solenoid. I bypassed solenoid so it will energize constantly. Subcooler temperature dropped and all temperatures dropped. All circuits on ticket now at 35 degrees. Checked out with manager on duty Francis. Complete | Compressors/Motors | Compressors/Motors | 0.99821
8/23/2023 2:03:48 AM Haddad, Masoud -0001 Arrived on site at 12:45am -no one on site , ring the bell in the front and the back in the receiving area and no one answered -no cars in the parking lot and no cars in the back where -called the dispatch and said he will push it for tomorrow -calm on follow up 8/23/2023 1:52:03 PM Porter, Joshua -0002 8/23/23 JP -Arrived on site and checked in with mod PA Went to LTA3-a to look into issues while looking at case was asked to look at the Main WIF due to shaking violently and having a loud noise. -Paused looking into case to deal with WIF -pulled case apart and found #2 fan at sensor not running and had short on pigtail looks to have been pinched by fan plenum. Repaired short and case at -9° now Cleaned up and checked out | Nuisance Calls | Compressors/Motors | 0.97022
7/28/23 JA TT-0800-0900 ST-0900 ET-1200 Little giant pump Model-N/A Serial-N/A Call was for water leak outside dairy cooler -upon arrival, checked in with MOD Fuller -Went to water leak and saw that water wasn’t leaking at the moment -Gained access to store’s scissor lift and while tech was on site, spotted with Scissor lift while driving it -Went up to water pumps and realized one was not working -Realized float was not activating water pump -Pump appeared to be bad -Called United refrigeration to order water pump and gave them all the info they need -Checked out with MOD Fuller and advised that pump will be ordered by next week -Call incomplete -Follow up needed | Compressors/Motors | Compressors/Motors | 0.9421
7/24/2023 5:44:07 PM Duran, Jason -0001 Arrived on site, checked in with management. There was a rain, thunderstorm in the area. I went inside and talked to the manager about if he would like for me to have work performed today after the storm has passed he said have a tech return tomorrow morning to take care of call. I got my signature and left store. Updated dispatch. Follow up needed 7/25/2023 4:37:40 PM Kurth, William -0002 arrived on location checked in with the receiving manager gained access to the roof top I found the unit not running so I put the unit in test mode and the one stage of cooling works fine so I took it out and ran down stairs to check on the hvac monitor and no units where communicating with the controller so I contacted novar and attempted to reestablish communication with the controller I was able to get a few units to communicate but novar was having issues getting them to consistently communicate I spoke with a couple colleagues and I found Adolfo has parts on order that should help the issues we are finding with the units. I informed the manager of my findings and checked out I will be returning Tomorrow to try and remedy the communication issues call incomplete this call is also related to this tracking number 251682915 7/26/2023 1:03:19 PM Kurth, William -0003 Arrived on location checked in with the receiving manager and gained access to the roof top once up to the roof top I disconnected every unit from the backnet and set all units to run as a stand alone unit and verified all set points for heating and cooling ran each unit in test mode and cycled power once done I double checked each unit to verify they where all running and then checked each area the units supply air to to verify the employees are noticing the difference to ensure everything is running properly once complete I cleaned up the roof top and checked out with the manager I also informed him the initial issue has an open work order that has parts ordered for this issue as of now no units are communicating with novar through backnet this work order is complete and is in relation to Customers PO# 249522736 251843464 251682915 The calls are all the same issue and will need closed 8/2/2023 3:14:50 PM Johnston, Andrew -0004 This issue is being resolved on work order 230801-0350/ 252502486 8/2/2023 3:19:10 PM Johnston, Andrew -0004 This issue is being resolved on work order 230801-0350/ 252502486 | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99513
7/24/2023 Bob E Survey damaged to inside safety poles in MTB2/3.poles are leaning on wall panels and concrete anchors are bent and not secure or holding. Will have to cut damaged anchors out seal holes with epoxy. Level floor with concrete epoxy and installed new bigger 5/8”x6” concrete anchors and secure anchors with epoxy. Will send in quote and do all repairs when quote is approved. Is a safety issue should be addressed asap. | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.99371
8/14/2023 7:59:48 AM Hanamornsate, Thirathanawat -0001 8/14/23 TH TT: 7:30-9:00 Time in: 9:00 Time out: 10:00 MTD 4.1-B: HUSSMANN MN: IC2SM8 SN: MY20B11524 Checked in with Service channel and MOD(Joe). Checked the location. Cases is running at temp and good airflow. Checked the both Coils are running at temp and no iced up the plate back wall. Checked both graph temp are good. Checked the History and Found its duplicated call with WO# 230813-0084. Informed and checked out with MOD (Joe) and Service channel. Job Finished | Nuisance Calls | Case Cleaning/Deicing | 0.90034
8/14/2023 8:26:39 PM Brooks, Brandon -0001 Sn# Sam’s Club 6610 Sc# 230814-0586 Po# 253718583 System: CS 8.4 Upon arrival checked in with MOD and ServiceChannel -Located case CS 8.4 -Actual case temperature within normal range -Verified proper sensor functioning by using ice bath -Sensor responding normally -Sensor covered in dust and debris -Cleaned sensor -Located dual temp switches in electrical room -DTC for CS 8.4 had been switched from normal temp to energy saving temp -Switched back to Normal temp -Verified case was at temp before departure -Informed MOD of work performed and obtained a signature before my departure. Job complete | Nuisance Calls | Nuisance Calls | 0.99789
Ti 1115 To 1600 4.75 regular Arrived and found rtu off. Checked controls and wiring found a short on the blower motor wire arching to ground. Repaired wiring everything is working properly. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99587
Assisted in the repair of condenser .. | Capital Replacement | Misc. Billable Repairs and Service Calls | 0.84756
8/19/2023 10:11:01 PM Schrock, Kevin -0001 Checked in with manager when I arrived. Found rack B not reading suction pressure and compressors in fault. After getting in touch with tech support, a manual input of 25psi was set on the rack and 3 of the 5 compressors manually shutdown. Also found CIM41 board offline. Could not get board back online and will have to follow up on Monday as Novar tech support is not available until then. Checked out with manager on duty and explained what was found. 8/22/2023 8:02:51 AM Schrock, Kevin -0002 Returned to store. After getting tech support on the phone, tested inputs of compressor board and verified that the transducer will need replaced. Checked CIM board operation and inputs and found that the board is good but store will need to have remodeling company out to fix sensor issues as they pertain directly to the freezer they are working on. Checked out with manager and explained what is going on. | Compressors/Motors | Compressors/Motors | 0.99773
Tt 0900-1030 labor 1030-1800 Checked in with Dutchess MTB 15 running high temp Found all 4 evaporators iced up, not draining water. Had store move product to gain access. Got spotters and moved scissor lift to cooler. Removed ice by isolating coils and running through defrosts. Could not use water due to product under coils, only got access to top shelf under coils. After insuring ice completely clear, blew out drain lines from inside cooler and then moved lift to outside of cooler and blew on each drain line from the outside as well. Each of them was stopped up with black sludge/debris. Drain pans were all in good shape, just build up inside the main drain. Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99865
7/24/2023 4:21:05 PM Biggs, Aaron -0001 Completed by another technician 7/24/2023 4:25:16 PM Jackman, Nick -0002 ST 1500-1730 Already on site for another wo Walked sales floor Found multiple bumpers track screws stripped Removed 1/4 self taping screws Installed 5/16 self taping screws Bumpers are now secure Walked sales floor with Erick Call complete | Non-Mechanical Door Repairs | Damage by Customer | 0.43804
Start time-1445 End time-1745 complete check in with manager Whitney checked freezer for iced up coils (no iced up coils) got roof access from manager checked roof unit for cafe freezer going off on high pressure took unit top off to get better access to Condenser coils cleaned condenser coils reset high pressure switch pressure sitting at 250 psi put top back on unit waited for freezer to get at temp checked out with manager Santiago Gonzaga | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.86862
Checked in with mgr at arrival. Went to motor room and proceeded with compressor replacement. We removed wiring from bad compressor along with oil regulator. We removed oil fail and pressure control. We detached compressor from mounting plates. We then removed compressor from bench. Next we installed the new compressor to the branch and secured in place with existing mounting bolts. We then wired in compressors and installed new oil regulator. We then installed new oil fail and pressure control. We ran vacuum on comp. We then started up comp and added oil. Comp now back online. There is no fork lift operator at this time. We will need to return in the morning to pick up comp and load on to the truck. FOLLOW IP REQUIRED travel:0700-0945 On site: 0945-1715 | Compressors/Motors | Compressors/Motors | 0.99856
Job completed. Arrived on site and found the compressor running. Went through the Novar board and found that the compressor tripped a couple days ago. Found the sight glass low on the compressor. Went to the reservoir and found it empty. Began checking pressure on my oil line and found a dip in pressure across the oil filter. Picked up new oil filter for the rack. Pumped down the oil line and isolated the filter. Changed out the filter and filter gasket. Put the filter back together and opened up the oil lines. Added one gallon of oil to the rack and confirmed the reservoir began filling up. The compressor is online and the rack has a sufficient amount of oil now. | Compressors/Motors | Compressors/Motors | 0.99853
7/15/23 Travel:10:45-11:15 Onsite:11:15-12:00 Checked in with manager Diana upon arrival. Found glass on freezer door cracked. Cover door with cardboard and got info needed for new door. Will submit quote for new door. 1 tech 6 hours 1 door 1 torque rod 1 torque master 1 hinge pin. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99669
Arrived to store let the manager know I was here to take a look at the look tow fan motors not running in the meat cooler walk in I then went to the cooler I got the scissor lift I got to the motors I saw the power off to all the motors I then looked and saw the fan blades were bent enough to where the wouldn’t spin so I went to united refrigeration I got one new fan blade cause that’s all they had I installed it and bent one of the old blades good enough to where it’ll work and move air I then turned the motors back on and there all running | Damage by Customer | Compressors/Motors | 0.99511
8/17/2023 3:50:15 PM HOLMES, JAMES -0001 1030-1300 2.5 hours reg time Arrived on site, checked in with Christy, found that bakery door handles booth broken along with door seal that holds heat tape in place, ordered parts will return to install 12/22/2023 8:31:34 AM HOLMES, JAMES -0003 0100-1400 4 hours reg time Arrived on site with new gasket and heat tape, new door handles for inside of door and outside, replaced damaged handles both functioning properly, replaced damaged gasket and heat tape, found that door has been hit with fork lift and bent so door wont close properly, talked with manager Matt and door needs replaced. Completing door work on another PO. Will submit a quote to replace entire door | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99675
Found compressor overheating due to dirty condenser and filters. Cleaned condenser, picked up and replaced filters and all checks ok. | Compressors/Motors | Compressors/Motors | 0.99742
8/5/2023 Rodriguez, Mateo -0001 Arrived on site and checked in with manager Jeffrey Located system MTB-S9.2 Upon arrival found fan casings full of water throughout the entire case Water was not allowing proper airflow thru the coils and temp was taking longer than normal to drop after defrost periods and causing ice build up Removed water from casings Little ice build up melted during defrost System should run normally now Checked out with manager Jeffrey | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
7/22/2023 12:04:10 AM Tobar, Ricardo -0001 At arrival checked into SC app and was allowed into store by John. Located bakery case not at temp. Bakery case middle section no airflow. Removed product, wire shelves and deck pans. Found evaporator fan motor non operational getting 115V. R/R motor. Fan back online, airflow restored. Temp at DA 36fdegs. Was allowed out by John. Unable to check out of SC app unable to verify case even when scanning QR code. Checked out via phone. Call complete. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.96518
8/16/2023 7:56:51 AM Authement, Corey -0001 Found compressor running but showing alarm found wires shorted repaired | Compressors/Motors | Compressors/Motors | 0.99861
Job is not complete. Have compressor and all parts needed arriving to united Brookhill on 8/7/23. Parts coming from Dallas. Arrive to store and check in with manager. Locate rack and found suction pressure running high. Check and verified all compressors online. Found BS1 off on digital scroll module for high discharge temp. Felt end bell of compressor and found extremely hot. Try pumping compressor down and valves will not hold. Call united and compressor with not be in until the 7th. Will return to install once parts arrive. Rack maintaining suction pressure for time being. | Compressors/Motors | Compressors/Motors | 0.99855
Aug 10, 2023 Leak checked all refrigeration equipment pertaining to the rack system. I started out at the rack houses. Inspected all compressors and lines. Inspected the u-benz and coil fins on the condenser coils. I did a thorough check of all walk-ins and refrigerated cases. Checked along honeycombs, the air return, and all visible lines that I could reach. No leaks found. | Nuisance Calls | Nuisance Calls | 0.99488
8/3/23 Sams 4735 230803-0319 252761476 TT 1515-1600 1600-1830 Arrived and checked in to service channel and manager. Working with tech Robert F. Assisting him with door repairs see his report for details. Complete | Non-Mechanical Door Repairs | Nuisance Calls | 0.9972
8/16/2023 8:13:07 PM Young, Roderick -0001 Job incomplete When to roof and and found the dehumidifiers 1&2 not working. Was able to power cycle the unit and got AHU2 back online. AHU1 has a short on the controls side and tripping the breaker #5. Will return to continue diagnosing. 8/18/2023 12:29:39 PM Young, Roderick -0002 Arrived on site and checked in with the manager. Went to the roof and found AHU1 not working. The controls breaker was tripping. Located the short and repaired it. Got the AHU back online and it is working properly. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.73157
7/27/2023 Jerry Mares GP# 230726-0370 TN# 251878713 0730-0830 TT 0830-1230 RT 1300-1430 RT Arrived onsite and checked in with management. Located System A05 ICC running high temp. Found all three cases running above 0 degrees. Case 2 was iced up from a clogged drain line. Removed product and panels to clear drain. Removed all ice from coil. Also removed ice buildup on case 3. Cleaned out trash from cases. Pulled out strainers and inspected. Found strainers on all three valves plugged up as well. Cleaned with degreaser and checked for leaks. Fired up cases and monitored operation. Temperatures dropped, cases maintaining SP. Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
Start time-1630 End time-1730 complete checked in with manager Sabine at temp upon arrival moved product to case MTB-11a took case apart to see if iced up (not iced up) called home office to see if call came in because of defrost temp 26 set point 25. defrost-Termination at 4 per day 25 min 45 degrees Changed set point from 25 to 28 and changed defrost 25 min to 35 min Checked out with manager Sabine | Nuisance Calls | Nuisance Calls | 0.99838
Arrived on site, checked in with manager. Went over to chicken prep walk-in cooler were the refrigerant alarm was going off. I used my leak detector to locate the leak inside cooler and wasn’t able to find any leaks. I reset the leak detector inside the cooler and the light kept going off. I then power cycled the leak detector at the box and after the alarm was still going off. Called novar to see if they could bypass the alarm until the replacement comes in, they could but the store would need to remove all product inside case due to the shit off of refrigerant going to cooler. I was able to manually turn off detector from main leak detector panel without shutting refrigerant to cooler. Updated management, cleaned up area of work. Parts on order. | Nuisance Calls | Misc. Billable Repairs and Service Calls | 0.70944
7/24/2023 7:29:22 PM Perez, Secundino -0001 07/24/23ZP SAMS CLUB 4704 Condenser A C -Got access to racks. -Pumped down rack C and shut off the condenser. -Began to wash out the condenser. -Turned the condenser on afterwards to dry it out and cycled the rack back on. -Pumped down rack A and shut off the condenser -Began to wash out the condenser -Turned the condenser on afterwards to dry it out and cycled the rack back on. -Waited for all case temps to drop. -This call is now complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99536
Arrived and cleaned the condenser for Rack B. removed the sprinkler and made sure all compressors were running. Discharge pressures were still high 320 psi. air flow is poor coming off the top of the fan motors and OK blowing out the side. fans are not oem. ordered new blades from heat craft and left the sprinkler on the condenser for now. | Compressors/Motors | Compressors/Motors | 0.96041
Arrived at the store, logged into Service Channel and spoke with the manager Justin. I accessed the roof and looked at the condenser unit for the grab and go case, and after checking all electrical, I found a fuse is blown on one of the main power legs at the disconnect. I removed the fuse and installed a new one. Turned the unit on and it is working properly now. Case is down set temp. I spoke to Justin and told him what I did and what I found. This is complete no need for follow-up. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.95021
1030-1300 Called out for BS11 comm loss Met with manager Gio Inspected and found case online and working. Spoke to home office who said case was in comm loss. Was transferred to novar Spoke to Novar and novar could not connect to rack controller. F/u to contact Novar again to diagnose issues with case | Nuisance Calls | Nuisance Calls | 0.99822
8/11/2023 6:17:19 PM Barajas, Armando -0001 Job completed. Spoke with manager and informed her why I was on site. She informed me what was needed. There was two lights damaged in the wall-in freezer (LTA-3). One light had just seemed to be twisted at the conduit. The other like had a broken light diffuser. Will need to refer this to an electrician who can gather the parts and do repairs. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99332
7/21/23 TH TT: 22:30-23:00 Time in: 23:00 Time out: 24:00 LTA-1 & LTA-2: Rollseal Door MN:6421-2283/ RS-500 Track Kit SN: 0009113 Checked in with Service channel and MOD(Melanie). Checked the location and found the Rollseal Door wasn’t all the way closed because the bad Door. It’s controlled by manual mode for now and already order the new Rollseal door with another work order. Checked the Manual operation. It’s working good. Keep to close all the way and temp going down but it not at temp. Needed to keep the door closing longer but the MOD(Melanie) not approve now because they want loading stuff from truck to the POS box. Informed and checked out with MOD (Melanie) and Service channel. Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9948
7/23/2023 7:37:51 PM Hanamornsate, Thirathanawat -0001 7/23/23 TH TT: 17300-18:15 Time in: 18:15 Time out: 20:00 C1 and C3: Dairy CLR Air Curtain HRC incorporated SN: 21-AL002 Checked in with Service channel and MOD(Karla). Went to Rack C. Condenser Coil is clean. Suction and Discharge pressure at set point. Liquid level is good and full sight glass. Checked the location. Found the Air curtain wasn’t strong and Found the Supply side grill was dirty. Found the Supply duct bend blew to unit C3 and C1 side. Cleaned the dust inside the supply grill. Bend the supply to Return grill. Adjusted the inverter to make a Supply air strong. Checked the temperature are good temp and keep going down. Cleaned the work area. Informed and checked out with MOD(Karla) and Service channel. Job finished | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99607
OT/TT1615-1645 OT1645-2015 Arrived on site checked in with Manager & SC Found System B19 At 54 Found door open Closed door monitored opps Case system dropped to temp Informed manager door must maintained close Found system RCU3 at 52 Asked for rooftop access Found RCU offline Had no power to RCU Found breaker panel open Located breaker found tripped Ohmed out compressor it’s good Checked fuses and contactors Checked for any visual shorts or rub outs Found none Restarted compressor Monitored opps System dropped to temp Checked out with Sabrina Call complete | Nuisance Calls | Non-Mechanical Door Repairs | 0.66757
TTST 0800-0915 Time in 0915 Time out 1330 I had shut down sub cooler because it was flooding out rack causing oil failures. I came back and provided assistance in getting sub cooler working again. Temperature sensors for sub cooler were reading incorrectly, replaced all sensors on sub cooler controller. Turned sub cooler on and it is now providing sub cooling on the liquid going out to circuits. Monitored to make sure it maintained proper super heat and did not over feed and flood out rack again. Compressor 2 and 3 are locked up on LRA, compressors will be changed in one of the multiple tickets open for this issue. Incomplete | Compressors/Motors | Compressors/Motors | 0.90551
Incomplete, parts on order. Case is missing metal piece that connects top of neighboring case together. Tech took pictures of what is missing from the front, top, and back of case, and also took photo of what is needed to complete this work order. Parts order email has been submitted and will return to complete work order once missing part has arrived. Model #: QLG1-12UN Serial: C17F01350 Type: coffin/bunker | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99606
Arrived to location, checked in with manager Kyle. Found roll up door displaying fault —-which is unknown position indicated. Opened access to door found door completely separated and not sitting in proper position looks like someone manually opened and closed door. With other techs assistance, manually fixed position of door. Once door was fixed, ran through troubleshooting. Found AC drive going in wrong direction. Found AC drive is bad. Door will have to manually be opened and closed untill new ac drive arrives. Checked with it with manager Kyle. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.94038
Sams 6685 Provo 8-3-23 Service call 230803-0042 Po 252718417 C11 a and B high temp Job complete On job 1500-1930 Found Case reading 98° and 67° Found 2 cases coil iced up Found cases not defrosting Deiced coil with hot water Replaced sensor with one Found in rack house Temp now reads Cases came down to temp Now goes into defrost Checked out with MOD Paul | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99849
7/29/23 Garrett Hunter Lta 7 running warm Upon arrival checked in with Mgr and service channel, went to bakery freezer found door switch had been knocked off the wall, causing solenoid to de energize, happened yesterday at some point, had another tech pull up graph for Temp history, repaired problem by moving the switch and resetting the actuation point, now when door is completely closed door no longer hits box of switch, watched box drop in temp checked out with mgr Claudia call complete | Damage by Customer | Damage by Customer | 0.97842
7/17/2023 2:35:26 PM Smith, Stephen -0001 En Route: 07:30 Time In: 08:15 Time Out: 12:30 8.2A-8.3A high temping Checked in with manager and found fans not running due to case cleaning the night before, staff forgot to plug fans back in which caused the high temp alarms. Plugged fans back in and temps are currently dropping. Job is complete. | Nuisance Calls | Nuisance Calls | 0.9624
7/23/2023 9:00:54 PM Monjaras, Daniel -0001 Checked in with manager Lee. Got tools down. Went inside store and located cafe WIC. Opened door and found no door handle from the inside. Found door handle that fell off. Inside new screws. Verified it’s not going to fall off. Verified they are able to open it from the inside cooler: Checked out with Lee. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9936
7/28/2023 5:00:21 PM Monsivaiz, Armando -0001 Checked in with service channel located asset tag. True self contained cooler in curbside running warm. Verified probes hooked up gauges checked condenser coil. Coil was dirty cleaned out checked evaporator fans. When diagnosing evaporator coil found the back of it iced up. Had to shut unit off overnight to clear ice on evaporator. Will have tech return following morning. Checked out with Veronica Luna and service channel. 8/1/2023 2:49:04 PM Meza, Nicasio -0004 Helped tech with R290 unit . 8/1/2023 3:56:44 PM Monsivaiz, Armando -0003 WO/ COMPLETE Return to site needed 2nd tech to move case to acces compressor. Verified restrictions on lines causing to run warm. Picked up 14oz of r290 propane as well new drier filter and fittings. Set on vacuum solder new components and pressurized with new gas. Cleaned up and put cooler back in its original place. Waited for case to reach temp checked out with and service manager. Checked in with service channel evaporator was clear waited for cooler to come down to temp but still not reaching setpoint. Will return to continue diagnosing. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99489
Sams 4730 West Jordan 8-3-23 Service call 230728-0217 Po 252076913 Power outage Job complete TT/OT 1930-2015 OT 2015-2115 TT/OT 2115-2145 Stayed with electrician during checks No parts are being replaced Power is to remain on tonight Electrician gave us go ahead to leave | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99577
7/16/2023 7:31:17 PM Brooks, Brandon -0001 Sn# Sam’s Club 6624 Sc# 230716-0090 Po# 250996461 System: LTA-2-Freezer Upon arrival checked in with MOD and ServiceChannel -Found RCU2 Cafe freezer coil fans off and at high temp -Gained access to roof -Located condenser unit on roof -Verified power on main breaker line and load side -Unit off on High Pressure -Reset High Pressure Control -Unit switched on -Running High Discharge Pressure -Only 1 of 2 fans running on condenser unit when powered on -Located fan wire running to main contactor -Found loose connection -Secured wire connection to contactor -Both fans running -Discharge Pressure returned to normal -Verified unit running properly -Verified normal temperature at Walk-in box -Informed MOD of work performed and obtained a signature before my departure. Job complete | Compressors/Motors | Compressors/Motors | 0.99266
Checked in with colt . went ahead and checked out the case and the case had a fan turned off because someone tried to put the plastic covers and the fan broke one of them and got stuck, fan wasnt running. case was also iced up. I turned off the valve and grabbed the blue water cart. Began to taking off the panels, after when I took them off I began spraying hot water, melted all the ice and cleaned up the case, took the blue cart to its place while the case dries up a little, after when I came back I put everything together and opened the valve on . Waited for the case to come down on temp. Temp is now at 34 degrees. Talked to Chris about the situation and checked out. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99731
7/25/23 TPP-AT-67-HC 10150628 -Arrived on site and checked into service channel and with MOD. -Located pizza prep table in food court. -Found outlet to case with a tear on wire exposing inner wires, some copper wire exposed, suspect wire was dragged across floor. -Too much slack on outlet wire causing it to be dragged around. -Covered exposed wire with vinyl tape and secured loose outlet wire to case with zip ties to prevent further damage. -All system ops ok at this time. -Job complete. | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.99672
Arrived on site checked in with the manager -checked A02 and A05 walk in freezers -found it’s at 7 degrees and 4 degrees -checked the evaporators and fans all fans are running -found some heavy frost on the evaporators -checked the receiver level and it’s good -checked high and low pressure and it was good -put A01, A02 and A05 on a defrost and after the defrost the temperature dropped to -1 -put on manual defrost again and all the frost on the evaporators melted and the temperature dropped again to -1 All checked good -call completed | Case Cleaning/Deicing | Misc. Billable Repairs and Service Calls | 0.61969
8/10 bt upon arrival found location of optical unit (unit #6). Went on roof, found unit in question. Found compressor running, found blower contactor pulled in but drawing no amps. Checked cabinet, blower not running. Evap iced up. Killed power, Ohmed leg to leg, found open. Pulled assembly, found motor base plate very in level. Removed motor, leveled base plate. Called Lennox. Motor was in stock. Went to supply house and picked up. Returned to store. Fought old pulley. Finally got off. Replaced motor. Verified level. Evened out pulleys. Put assembly back, put new AX44 belt. Verified ice off of coil. Turned on, verified rotation. Waited till unit kicked on. Verified pressures. Good to go. | Compressors/Motors | Capital Replacement | 0.51708
08/07/2023 Sorin Clichici ST/TT # 0900-1000 Check in # 1000 Check out # 1300 True Model # TTP-AT-67-HC Serial # 10169080 Pizzeria Self contained unit Upon Arrival check in with store manager and SCP Gain access to pizzeria found refrigerator overload with products advise personal working there to move on pizzeria cooler Food storage on the bottom of the refrigerator (shelf are not in position) disconnect refrigerator from power supply remove unit front grill ,found condenser very dirty . remove front evaporator panel and evaporator motor fan found iced up evaporator water inside of the pan start to remove ice from drain pan noted drain line clog clear evaporator drain line , remove all ice Tested with water all ok water goes free blow clean the condenser using nitrogen reinstall all parts back clean remove all water accumulated inside of the fridge remove condensate water pan , clean wash and install a set of wicking pads reinstall back both shelves Power on the fridge , cycle well at 31.0F cut out 35.O F cut in Call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
7/14/2023 4:19:30 PM Perez, Secundino -0001 07/14/23ZP SAMS CLUB 4703 System MTB2b -Got access to the WIC -Requested for product to be removed from shelving. -Got access to the coil and found water build up. -Removed union and water began to drain. Put the drain back together -Went to get a 5 gallon bucket. -Began to drain the water from the drain pan. -Empty water and began to drain remaining water. -Cleaned up water -Located the mod and informed them of the situation -This call is now complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99841
Jul 24, 2023 Cleaned the condenser for rack B. Removed the sprinkler and made sure all compressors were running. Discharge pressures were still high 320 psi. Air flow is poor coming off the top of the fan motors and OK blowing out the side. Fans are not on. Ordered new blades from heat craft and left the sprinkler on the condenser for now. Aug 30, 2023 Replaced all 6 condenser fan blades on rack B condenser. Air flow has improved and discharge pressure is running 240-250. | Compressors/Motors | Compressors/Motors | 0.8613
8/3/2023 10:47:04 AM Maldonado, Chris -0001 Start time-1130 End time-1245 complete check in with manager Jay Perez cafe exhaust is working lights on the exhaust assembly is not working put a new bulb in socket still didn’t work, switch getting power, no power going to the lightbulb socket advise manager jay perez to get an electrician out to have a look at it checked out with manager jay perez | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99654
Arrived on site checked in with the manager -found the walk in cooler in the cafe on high temperature -walk in cooler MT-1 -found the condenser on the roof is down -after troubleshooting found the high pressure switch is tripped -found the condenser coil dirty -cleaned the condenser coil and reset the pressure switch and the unit start running and start cooling -waited till reached 37 degrees -condenser fan running normally -checked pressure and no restriction found and the pressure is normal -all checked good -calm completed | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.85494
Upon arrival located manager to start Job went to case case was running warm went to motor room to check Novar case was in defrost watch case come out of defrost pull down the temperature all OK at this time complete | Nuisance Calls | Nuisance Calls | 0.99825
On-site 1015-1230 Arrived on site. Checked in with manager, Jacob. Model: TD600-081-VC-4-FHSLX-B Serial: 1201000039 R407a refrigerant Made way to motor room to check rackB. Receiver level is at 30-35 Suction pressure @ 41psi Discharge pressure @ 280psi Transducers are reading correct pressures Monitored rack as compressors cycled to check receiver level All cases are reaching desired set points Receiver level dropped to 20% while monitoring Will return tomorrow to add refrigerant and perform leak search on rackB job incomplete | Compressors/Motors | Compressors/Motors | 0.99856
Checked in with manager Lee. Got tools down. Went inside store and located cafe WIC. Opened door and found no door handle from the inside. Found door handle that fell off. Inside new screws. Verified it’s not going to fall off. Verified they are able to open it from the inside cooler: Checked out with Lee. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99597
Completed arrived met with manager. Repaired 5 different pipe insulation tubes. | Misc. Billable Repairs and Service Calls | Compressors/Motors | 0.64641
Jul 19, 2023 Found water leaking from under case. Drains clear and drain pan empty. Found case is installed with drains piped to the wrong side of case rail. Cut drains out and repiped into floor sink. Cleaned water and soak pads up, dried floor. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
08/03/23 Noe Lopez Travel: 1300 Arrival: 1500 Departure: 2000 System: S/C Case MT -Checked in with MOD -Went to inspect case noticed airflow was hot -Went to inspect the compressor and condenser fan -Both were off -Went to check the compressor 3 legs all showing compressor was in good standings -Checked wire 23 for the leg that feeds the compressor and start up -Red wire that was only pulling 20 volts -Conducted a wire trace to see where the breaker was attached -Traced the wire to breaker LD4 on 39 -Tried to pull breaker to on position, breaker would not pull to on -Informed manager to call in a electrician to repair breaker -Per management she informed me that she would have him put the wire that is currently on 14 need it back on 23 when done -Amperage on 14 is currently 6 -Job complete | Compressors/Motors | Compressors/Motors | 0.99868
7/23/2023 5:56:33 PM Calderon, Jose -0001 Checked in with manager Julie, the compressors are tripping on oil. The oil pressure is off on the whole rack, so the rack needs a whole compressor oil change and filter clean. The cases are at temp now but it will trip on oil, the oil is black. compressors 3 and 4 are running without interruption however this rack needs a full oil change. RACK B MODEL #PS425SMRAD SERIAL # 25417-129 Compressor 3 MODEL # 06DM3370DA3650 SERIAL # 6DKERC4R2J41 COMPRESSOR 4 MODEL # 06EM775600 SERIAL # 6EBCBD1E2C41 Let the manager know that they need to place a work order to do a whole rack oil change, the oil looks black in the sight glass and compressors keep tripping on oil. The rack is no longer in lock out and all the compressors are running. Checked out with manager Julie Call Complete 7/23/2023 9:41:38 PM Calderon, Jose -0002 N/A | Compressors/Motors | Compressors/Motors | 0.99858
Checked temperature and case is at setpoint temperature. Manager on duty Payne told me to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.99757
Jul 27, 2023 Found fan stuck in ice for break room freezer and drain plugged with ice building up from drain line. Deiced drain line. Ran freezer through a defrost, all heaters and drain heater working. Put case back together, freezer is back down to 0 degrees and dropping. I had Novar program comp 5 for A rack, from normally open to normally closed. Comp 5 now back online for A rack. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
Called out to check cases running high temp. Upon arrival found tech had already run the call earlier this morning. Walked store. Everything seems to be working fine. | Nuisance Calls | Nuisance Calls | 0.99815
8/3/2023 3:34:58 PM Stuart, Christopher -0001 En Route: 1245 Time In: 1330 Time Out: 1515 MTD Rack Comp 3 L/O Gained access to the roof. All compressors on MTD rack are online. Compressor 3 drawing 17 amps. Rack pressures @ 33/319. No issues found. Job Complete | Compressors/Motors | Compressors/Motors | 0.9986
7/31/2023 7:28:06 PM Garreans, David -0001 Checked temperature and case is at setpoint temperature. Manager on duty Payne told me to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.99793
8/18/2023 2:17:11 PM Kaser, Wade -0001 Incomplete, parts on order. Tech inspected fans in meat prep room that was making “loud noises”. Tech turned fans off, removed fan covers to inspect and make sure nothing is interfering with fans, tech saw nothing interfering the fans. Tech found source of “loud noise”. Tech deemed that fan motor was wearing out and will need to be replaced as soon as possible or fan will continue to make loud noise and need to be replaced soon. Model number of motor: F2208A3955S Serial: 15092200076 Tech has parts in hand, tech checked on fan to make it was still running and temp is holding, everything is normal. Tech will return following Monday to replace fan motor 8/21/2023 4:28:38 PM Kaser, Wade -0002 Completed. New fan motor and fan blade installed, unit is no longer making loud noises. | Compressors/Motors | Compressors/Motors | 0.99808
Rack B Kysor warren Model -TC430-056-DC-4-NVG-B Serial -0203000236 Checked in with manager on arrival. Call placed for high suction pressure on rack B. Gained access to rack and checked OPS at co troller. Found BS group running @ 49 # suction . Spoke with home office and found no active alarms on rack B. Ensured compressors are online nothing tripped. Checked suction valves at compressors and ensured no valves blowing by. Gauged up to rack and ensured transcode pressure. | Compressors/Motors | Compressors/Motors | 0.99827
8/11/2023 6:14:04 PM Sanchez, Cristian -0001 Travel 1430-1500 Labor 1500-1630 Travel from 1630-1745 Checked in with MOD Removed water from drain pan Diagnosed faulty drain pan heater New drain pan assembly expedited ETA Monday 08/14/23 Follow up needed 8/15/2023 6:28:34 PM Franco, Ryan -0002 On site. Labor: 1415-1745 Travel from: 1745-1815 Began coating of the drain pans float. This time using a “high heat” coating rated for 1200°f. Made multiple applications about every 15minutes. Worked on Gro freezer A3 in between coatings. Fans not running, found a switch off. A02 and A03 freezer operating normally. Final coating made at 1700. Will come back tomorrow evening when float is tack free. Follow-up. 8/17/2023 8:47:10 PM Franco, Ryan -0003 Travel to: 1600-1630 Labor: 1630-1800 Travel from: 1800-1830 Replaced pan with coated float. Tested. Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.98007
8/11/2023 5:03:57 AM Touchet, Benjamin -0001 8/10 bt upon arrival found location of optical unit (unit #6). Went on roof, found unit in question. Found compressor running, found blower contactor pulled in but drawing no amps. Checked cabinet, blower not running. Evap iced up. Killed power, Ohmed leg to leg, found open. Pulled assembly, found motor base plate very in level. Removed motor, leveled base plate. Called Lennox. Motor was in stock. Went to supply house and picked up. Returned to store. Fought old pulley. Finally got off. Replaced motor. Verified level. Evened out pulleys. Put assembly back, put new AX44 belt. Verified ice off of coil. Turned on, verified rotation. Waited till unit kicked on. Verified pressures. Good to go. | Compressors/Motors | Capital Replacement | 0.67268
We replaced one compressor and will return to replace the second | Compressors/Motors | Compressors/Motors | 0.99839
7/21/2023 10:54:39 AM Alvarado, Christopher -0001 Arrived to job located racks on side of building. Accessed rack b comp 1 staging on and off as it should still showing alarm. Need to order a new current transformer. Will return to install. 9/5/2023 10:24:29 AM Alvarado, Christopher -0002 Arrived to job located rack b. Turned power off to compressor one replaced current transformer. Powered compressor back on. Called Sams support had them force compressor one on. Compressor operating and showing current on novar now. | Compressors/Motors | Compressors/Motors | 0.99855
7/14/2023 2:31:13 PM Brandau, Kenneth -0001 Arrived at the store logged into Service Channel and spoke with the manager, Antonio. I looked at the bakery door and the bottom track mount was crooked. Stopping the door from opening. I adjusted the mount and re-secured it. So now the door opens smoothly. I spoke to Antonio and told him what I did and what I found. This is complete no need for follow up. | Non-Mechanical Door Repairs | Damage by Customer | 0.79041
Checked in with manager Tanya, ordered fans and submitted quote for parts with Lawrence. Let the manager know that the parts are in quote status Checked out with manager Tanya submitted quote Call Complete | Capital Replacement | Nuisance Calls | 0.72095
7/21/2023 5:23:04 PM Rodriguez, Roberto -0001 Checked in with the Site Manager. I checked the MTC Open Case Cooler. The temp on C15C is currently at 25 Degrees F. I checked the Compressor Rack for this Unit and Everything is working OK. 8:00Am-8:45Am Travel 8:45Am-4:00Pm Labor 4:00Pm-4:30Pm OT Labor | Nuisance Calls | Nuisance Calls | 0.97151
8/1/2023 4:59:13 AM Jennings, Jeromy -0001 Job completed Was currently on site for another job spoke with the manager and she told me that they were having issues opening and closing this door to the freezer and I adjusted several places on the door to close up the gap. Got gas closed up. Everything is good at this time . | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.68991
8/23/2023 11:14:21 PM Oleary, Holden -0001 Arrived on site and checked in with manager Nick. Started going over everything asked on service channel. B-13 case high temping at 90°. B-19 case hi temping at 41° and LT-SC IC DRS high temping at 8°F. Started with the LT-SC IC DRS case to make sure product was not in danger. After further investigation, found that there are two cases/circuits that are labeled the same one is under rack B the other one is under rack A. After calling Novar found that rack A circuit controls the RCU unit on top of the roof that controls the actual ice cream doors behind the three main POS freezers and cooler. After further investigation in order to find the second circuit due to nothing being labeled. Finally, after going through the store was able to find that the curb side pick up Freezer is the one labeled under rack B. Labeled the case above the temp controller on case for both cooler and freezer. Case is iced up and getting very little airflow and temping currently at 6°F Case LT-SC IC DRS Self contained Brand -Heatcraft Model -QIV5V14-03AMUN Serial -C16B01356 After diagnosing, the unit found that the condenser was extremely packed and could not have airflow through the coils, causing the refrigerant not to condense properly and causing icing issues on the evaporator coil, due to flood back. Once condenser coil was cleaned properly and blown out with CO2 due to the case, being a self-contained and not being able to deice properly using a hose and water in fear of flooding, spoke with manager and decided to turn off the case while further diagnosing other cases that are temping incorrectly. Opened all the doors removed the panels and allowed Ambient temperature to penetrate case in order to defrost naturally. Let case defrost and checked the heating element operation and the programming based on manufacturing specs and everything was running good just the issue with the condenser being dirty seems to be the only issue with the case. Turned case back on before leaving and running through another defrost cycle and gave the manager the all clear of case is at temp in the morning to start using. Started further diagnosing circuit B-19 case Brand -Heatcraft Model -DX6XN-08RUN Serial -C16A00839 Case has multiple work orders opened under this issue that was quoted for work to be done called Novar and was going over case programming and controls. Found case was completely iced up and had no airflow at all. Started deicing and going over controls and setpoints with novar. After case was deiced started checking valves and superheats after further investigation and checking with previous technicians found that the case needs new TXVs that were already ordered. Making sure defrost and everything was working properly will complete parts install on work order 230801-0310 and TN 252496960. Started going over the B-13 case which is high temping as well at 90°F. B-13 case is the MD Pizza case located in front of the cafe. Case controller upon initial look over is at 29°F which is the setpoint for this case. Started taking apart the case to further diagnose, found that the honeycombs were extremely dirty and needed to be blown out and can cause lack of airflow. Found case was temping properly, but not showing correctly on Novar rack controller for circuit monitoring. Brand -Hussmann Model -?2???6XE Serial -?000162142 Started taking apart panels and tracing temp sensor making sure there’s no disconnect. Case module is reading proper case temperature but monitoring is still reading 90°F. How to take apart drain line and bottom of case in order to access 1081 opus controller. Did not find any issues with sensor or terminal points. Going back-and-forth between electrical room controller back to case found that under rack control monitoring, case sensor is reading properly at 29.7°F but control temp is reading 90°F with sensor fault possible that case control board is bad. Called novar after resetting opus controller and waiting the time for case to reset. Once case reset correct temp came up on the rack monitoring. Made sure case continued to operate correctly and updated manager call is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
Start time-0700 End time-1800 check in with manager Matthew queen found compressor MTB #5 in back receiving, called united to verified that we have the right compressor verified compressor had no power closed all valves to compressor verified no pressure left in compressor drain all oil from compressor unwired, unbolt compressor took old compressor off b rack and put new compressor in wired and bolt new compressor, leak check wired in new DP340240F DEFINITE PURPOSE CONTACTOR 3 POLE 40 FLA 240 VAC COIL, Auxiliary Switch 1950243 pulled vacuum, open system, leak checked once more turned on the breaker compressor did not turn on. called home office to verify that the compressor is on (yes) follow up for high level teach check out with manager Matthew queen | Compressors/Motors | Compressors/Motors | 0.9986
7-19-23 Paul Z / ventilation motors out on rack B Rack B checked in with Jeremy found motors not running called supply house located 1 and orders other 3 will replace all run capacitor also Replaced one motor and two capacitor today follow up on Monday when parts arrive Incomplete | Compressors/Motors | Compressors/Motors | 0.9981
Replaced door gasket and relocated defrost termination sensor | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99619
Favian Porrata 07-25-23 Arrival 1545 Departure 1700 Upon arrival checked in with Manager Peter. Call was for Ac by check is not blowing. When doing my inspection of the Ac unit. Check split and and a 24 split. Check to make sure all compressors where on. Made sure all condenser fans where running. Checked pressures. Everything checked ac is running. Call complete. | Nuisance Calls | Nuisance Calls | 0.99811
7/27/2023 6:43:18 AM Ceja, Mario -0001 Arrived on site checked in with manager and service channel.located rack c . Found compressor 4 turned off . Checked all electrical and compressor. No issues wrong . Turned compressor on and rack liquid levels are at 30% . Found no signs of low liquid levels low . No alarms at this time . No further issues all cases at temp . Job complete | Compressors/Motors | Compressors/Motors | 0.96685
Checked out freezer and question. Found ice everywhere. Ran system through defrost deiced with torch blew out drain line found plugged with dirt trash cleaned up ice. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9984
7/21/2023 1 PM La Cava, William -0001 7/21/23 Sams 6614 230721-0266 251517319 Working with tech Robert F. We repaired the Meat cooler door see his notes for details 7/21/2023 Frietze, Robert -0002 Meat Cooler MTB-15 Rail Damaged 7/21/2023 Robert F Bill L Already onsite and checked into ivr and with mod. Meat cooler bottom guide rail is damaged and coming off. Removed screws and removed bottom guide rail. Then used grinder to remove broken screws in door. Used drill bit to pre drill holes in stainless steel to mount new bottom guide rail off of truck stock. Used new self drilling screws to attach new bottom guide rail to door. Found top of bent out and not sealing. Used ladder and adjusted door for best operations and closed gap in door. Checked door operations several times and door is working properly now. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99684
Arrived at the store, logged into Service Channel and spoke with the manager Stacy. I looked at the walk-in freezers and all fans are working properly. I spoke to Stacy and told her what I found and what I did. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99804
8/22/2023 8:22:35 PM Soto, David -0001 MTA-8 Meat WIC -While on site looked at walk in cooler for water leaking -found drain pan bent and screw mount damaged causing drain to sag -bent drain back and secured pan to coil mount -job complete | Damage by Customer | Case Cleaning/Deicing | 0.99849
082223 Alfredo Receiver level alarm System B TT/ST-0830-0930 ST-0930-1030 Arrived at location and checked in with service channel and store manager. Checked receiver level for rack B and found it at 25%. Called home office to verify and agent stated not only reading low receiver level at -19% but also Al compressors not on and at 0psi. Agent advices to do a power cycle to reset controller. Powered cycle controller and called home office. Agent stated still same readings. Informed agent receiver level at 25%, suction pressure at 20psi and all compressors working. Informed agent novar reading controller not set up yet and still under old controller. Call completed. | Compressors/Motors | Compressors/Motors | 0.99844
Checked in with mod found no airflow on case. Manager told me that water build up due to clogged drain. Replaced both burned motors and de iced coil. Put system back together and watched temperature drop. Job is complete. Asset Categories: Refrigerated Equipment. Root cause(s): Normal Wear Tear. Resolution code(s): Replace Evaporator Fan Motor check out with store mod job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99812
Found drain line on tower needs to be reinsulated. Also found leak on water line above insulated line. Will have to order drain insulation. Will proceed with this once parts come in. All parts will be at United except for the 7/8 pipe as we do not need a full stick. Just a small piece. Rack A line sets 1 1/8 coupling 1 1/8 st 90 x 2 Bushing 1 1/8 to 7/8 7/8 LR 90 x 3 7/8 pipe 5ft 7/8 w 1/2 wall 1 stick 1 1/8 w 1/2 wall 1 stick 30ft w 1/2 wall 3 1/4” Black duct tape | Misc. Billable Repairs and Service Calls | Case Cleaning/Deicing | 0.99717
7/21/2023 4:12:59 PM Garreans, David -0001 TTST 0830-1000 Time in 1000 Time out 1815 Checked in with manager Alberto. Rack C breaker had tripped due to bad compressor 3. Tech Lit will turn in information for a quote to replace on his ticket that he is on. Compressors were not staging correctly. Was on phone all day with Novar getting staging corrected and they put in an override off on compressor 3 so it will not try calling for it on staging. When compressor gets changed Novar will have to put back into staging. Suction pressure came down and all temperatures on rack C dropped out of alarm. Checked out with manager Marcus. Complete | Compressors/Motors | Compressors/Motors | 0.99857
7/24/23 TH TT: 8:00-9:00 Time in: 9:00 Time out: 10:00 MTC-6a: Meat prep Heatcraft MN: WK155AC SN: D06D03308 MTC-06b: Heatcraft MN: WK155AC SN: D06D03307 Checked in with Service channel and MOD (Marcus). Checked the location and both coils are clean and good airflow. Checked Suction and Discharge pressure are good. Checked the temperature and both units are good temperature. Set point is 43 degrees F and both unit are 44 and 45 degrees F. No Alarm present. No found issues. Informed and checked out with MOD(Marcus) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99831
Aug 02, 2023 Found Condenser dirty and needs new motor. Will return to install. Aug 03, 2023 Replaced condenser fan motor and flan blade. Cleaned coil that was full of grease and dirt. Case has dropped in temp and functioning properly. | Compressors/Motors | Compressors/Motors | 0.99806
TT/ST 0730-0800 ST 0800-1345 Returned to store with parts Replaced compressor B1 Replacd Contactor Replaced auxiliary switch Pumped in 1 gallon of poe 68 Leak checked with bubbles Let compressor run 2nd Leak check electronic leak detector No leaks found Compressor running between 7 and 8 amps On each leg Checked ops OK Took old Compressor for core return | Compressors/Motors | Compressors/Motors | 0.9986
OT TT:18:30-20:30 OT:20:30-00:00 OT:00:00-2:00 OT TT:2:00-4:00 Arrived checked in with MOD, made way to Rack B and found rack completely down, found compressors in lock out due to high head pressure, made way to condensers and noticed that they were covered in dirt and debris, cleaned condensers for all three racks, reset rack b and still no condenser fans coming on, called Jose he advised to bypass the VFD on controller so I did and put to 60k htz. So that they would stay on this call will need Jim to follow up please since I’m not that diverse on glycol racks yet. Call needs follow up by Jim. | Compressors/Motors | Compressors/Motors | 0.9984
8/7/23 arrived on site and checked in with MOD. Went to case and found case hot and no refrigeration present. Went to roof and found unit off on high head pressure with a manual reset. May need to replace high pressure switch. Reset unit and placed in service. Unit is back in service and temperature is dropping. | Compressors/Motors | Compressors/Motors | 0.99768
Arrived on site and checked in with the manager. Went to the roof and found AHU1 not working. The controls breaker was tripping. Located the short and repaired it. Got the AHU back online and it is working properly. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.99805
Incomplete Arrived onsite, waited on Sam’s employees to move pallet for door and rail track. Unboxed rail and door. Went to door needing replacement and began uninstalling process. Used ladders to unhinge walk in door. And uninstalled old railing track. Waited on forklift operator to help carry door out to receiving. Forklift operator help move new door to site. Brought old railing out to outside receiving. Began installing new railing. Used scissor to install. Cleaned up package trash. Will return Wednesday with trailer to pick up door and crates. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99711
8/4/2023 10:19:28 AM Simon, Devin -0003 Assisted Cory A. with walk-in freezer and walk-in cooler 8/4 Entered in to Service Channel by Corey Authement Checked fan making noise will help to remove assembly Remove covers off of assembly found no broken parts the motor is vibrating bearing are nad meed to be replaced will need to order motor. 8/3 Entered in to Service Channel by Corey Authement Checked fan making noise will need help to remove vent assembly 9/19/2023 9:50:42 AM Authement, Corey -0006 Motor has been order at Granger Laffayette will be 9 /22/23 9/21/2023 9:52:58 AM Authement, Corey -0007 Installed new motor tested ok amps good | Compressors/Motors | Compressors/Motors | 0.99761
20:00 pm -12:45 am (4.75 Hours AFH) Arrived on site and checked in with MOD. Waited for customers to leave store. Grabbed scissor lift and ran hoses to dairy cooler. C18 was the most iced up evaporator. De iced case and got zamboni machine to clean up water in cooler. Adjusted TXV and air curtain for case. Put evaporator back together and cleaned up cooler/ work area. Will return to check on evaporators and make sure theyre working fully. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
8/16/2023 2:12:32 PM Toomer, Collin -0001 ST:13:30-14:45 Arrived checked in with Loc Found bakery freezer LTA-9 In the back of store Found that the door and the box wall are damaged really bad and the handle is broken. Not all won’t the door to close fully.Spoke with Jose and he advised. KPS comes out and replace door and framing. Spoke with manager he said every time he puts in the call they send us. Spoke with travis, he advised that we need to escalate to another provider KPS to repair the door. No work can be done at this time. No asset tag on the door, can’t find case number other that LTA-9 Job completed. Checked out with Loc | Non-Mechanical Door Repairs | Damage by Customer | 0.98664
complete checked in with manager checked case for temp. (Running at temp 31) checked history was complete on 07-22 checked out with manager | Nuisance Calls | Nuisance Calls | 0.99821
MTB -Arrived on site and checked in with store -found compressor had already been swapped out -appears to be have done under warranty by another contractor -contactor auxiliaries and pressure controls were all still original and not changed out -removed and replaced contactor and auxiliary -pressure controls not available until oct.31 -see 2nd tech notes for further information | Compressors/Motors | Compressors/Motors | 0.99839
7/17/23 TH TT: 8:00-9:00 Time in: 9:00 Time out: 10:00 MT-BS-1-B: HUSSMANN MN: ID5SM12 SN: MY18F044846 Checked in with Service channel and MOD (Alex). Checked the location. The case is good airflow. Checked the monitor. The case is at temperature (31 Degrees F). Checked history alarm page and No found alarm on this case. Checked graph temp is good. Informed and checked out with MOD(Brad) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.9984
8/1/2023 3:10:47 PM Alcaraz, Jose -0001 TT 0730-0900 St 0900-1100 Call completed Arrived log into service channel and check in with manager for produce WIC high temp -check controller found circuits going into defrost and the same time -called Novar had them change defrost to schedule defrost with a 10 min delay before the next circuit goes into defrost -waited for cases to drop temp | Nuisance Calls | Nuisance Calls | 0.99837
Installed new motor tested ok amps good | Compressors/Motors | Compressors/Motors | 0.99733
TTST 1300-1400 On-site 1400-1730 Checked in with manager on arrival Checked Rack A VFD. Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643. Checked and reconnect vfd. Restarted and check and found the vfd working normally and found the cooling fan bad checked rack C&D vfd in bypass they also have hbad cooling fans. I will order cooling fans the vfds were turned off during during the summer. Parts on order. Fan assembly’s for danfoss vfd. Incomplete parts order | Compressors/Motors | Compressors/Motors | 0.99623
7/16/2023 1:03:27 AM Pena, Daniel -0001 Arrived on site checked in with Manager SC Found System B19 At 54 Found door open Closed door monitored opps Case system dropped to temp Informed manager door must maintained close Found system RCU3 at 52 Asked for rooftop access Found RCU offline Had no power to RCU Found breaker panel open Located breaker found tripped Ohmed out compressor it’s good Checked fuses and contactors Checked for any visual shorts or rub outs Found none Restarted compressor Monitored opps System dropped to temp Checked out with Sabrina Call complete | Nuisance Calls | Non-Mechanical Door Repairs | 0.76478
8/15/2023 1:12:17 PM Edwards, John -0002 Assisted technician on site. 8/15/2023 2:55:23 PM Nichols, Cooper -0001 Call was for suction alarm on rack B Went over all ops and found nothing wrong Everything is operating good at this time No alarms @ arrival and none @ departure | Nuisance Calls | Nuisance Calls | 0.99824
John Edwards 07-31-23 Travel 1515 Arrival 1630 Departure 1700 MTPR System C6a,b On arrival checked in with MOD. Called home office and confirmed parameters. Defrost set to 4x45. Prep area at 50 and coils clear. Call complete. | Nuisance Calls | Nuisance Calls | 0.99821
7-25 Scotty Sparks Travel time 0745-0815 On site 0815-1800 Travel time home 1800-1830 Checked in and out with Leo Checked opes on door. Store hit new door with a pallet jack. Had to realign wall and secure wall. Readjust door. Realigned door strike. Door works like it’s supposed to. All opes ok. Job completed. | Damage by Customer | Damage by Customer | 0.81966
8/1/2023 1:01:00 PM Gary, Raymond -0001 8/1/23 Ray Gary Arrived onsite and checked in with the manager (Rae) I found the door hinge busted in half Because of the hazard the freezer cannot be used I tryed to see if I could get a temporary fix It worked but I was unsure of it so I removed it I didn’t want an employee getting Hurt I sent Mr Reyes all the information needed to get the hinge I’m seeking it to be expedited THIS JOB IS ON PARTS HOLD 8/15/2023 1:08:34 PM Barker, Kenneth -0002 Removed all damage broken hinge. Installed new hinge from van stock. Talked with Andrea showed her progress. Job complete.cleaned off graffiti from door | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99452
7/19/2023 5:31:50 PM Richardson, Preston -0001 Water leak in dairy cooler Checked in with MOD Got scissor lift access and store spotter Found water leaking from unit MTC1 2 Both units Fans running Turned off C1 dropped both coil drain pans found gunk build up in both coil pans washed and cleaned both pans found gunk frozen bottom of coil used map gas to de ice it off. Top inside of coil dirty brushed and used CO2 to clear dust off coil put unit back turned fans on. Turned off C2 Opened up unit found coil drain pans dirty cleaned and rinsed pans deiced junk off bottom of coil with Map gas inside coil dirty brushed and used CO2 put unit back fans running. Found water leaking from fire sprinkler notified MOD to get plugging out right away to fix that problem Checked out with MOD CALL COMPLETE | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99842
7/20/2023 2:06:06 PM Paruleski, John -0001 Called out for rack b comp offline Met with manager Jen Inspected compressor, shut down and pulled oil screen. Cleaned. Got compressor online. F/ u to RR Sentronic oil sensor. Ordered from ARS refrigeration, ETA 7/24 8/2/2023 7:00:10 AM Paruleski, John -0002 Called out to RR sentronic sensor Picked up parts locally Returned to site, removed and replaced sensor. Got compressor B1 back online All ops check good on departure | Compressors/Motors | Compressors/Motors | 0.99854
Time in: 1515 Time out: 1700 Checked in with MOD Went to Dr. office A/C didn’t seem to be running and was hot in there Accessed roof Went to RTU 22 and RTU 14 above dr. Office Both compressor off on high pressure and fans not running Reset compressors and got them running as well as the fans Condensers on u it’s extremely dirty Washed off condensers Went back into building to go to dr. Office A/C back on and cooling office Checked out with MOD Call complete | Compressors/Motors | Compressors/Motors | 0.99822
7/28/2023 10:49:42 AM Rivera, David -0001 7/28/2023. David Rivera Checked in found ladder made adjustments to curtain return ladder and cleaned up job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99496
8/18/2023 11:56:07 PM Hanamornsate, Thirathanawat -0001 8/18/23 TH TT: 22:00-23:15 Time in: 23:15 Time out: 00:30 FC1-1: Grab and Go CSC Worldwide MN: C3NBRSS48-S4P SN: 205829 Checked in with Service channel and MOD (Kurt). Checked the location. Case temp showed 46 degrees F and not strong Airflow. Take the product out and Evap Coil is clean and no iced. Found Honey combs and Condenser Coil were dirty and Cleaned them. Verify temperature sensor with water iced and Found bad temperature sensor. Picked up new temperature sensor in my truck stock. Replaced the new temperature sensor and verified it with water iced. It’s read correct temp. Checked the Compressor cut in at 40 Degree F and cut out at 36 Degree F. Checked the Temperature at case showed between 37 to 40 Degrees F. Cleaned work area. Informed and checked out with MOD (Kurt) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
Arrived on site, called for secondary tech assistance, utilized ladders for door access to control panel, door had no power, found power to door, but door wouldn’t open or close completely. Removed main door panel off, checked all sensors, rolled door down manually, and found large piece of plastic wrap obstructing sensors, put everything back together. Door is now operating as should. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98607
7/14/23 TH Time in: 10:00 Time out: 12:30 CS-12 HUSSMANN MN: IC2SM12 SN; MY18F044806 Arrived on site and checked in with Service channel and mod (Alex). Checked the location. Found case bad airflow. Take the product, Cover plates, Deck pans and shelves out. Closed the liquid line valve. Plugged out all fan plugs. Used bucket contain hot water and Deiced 3 Coils. Found drain pipe was slowly drained and flushed it by CO2. Cleaned drain pan. Put the plates back wall back. Plugged in all Fan plugs. Opened the liquid line valve. Put Deck pans, Cover plates and shelves back. Checked the temperature showed 32 degrees F. Cleaned work area. Informed and checked out with MOD(Brad) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99834
OT TT:17:00-19:00 OT:19:00-20:00 Arrived checked in with manager suman, proceeded to the rotisserie preparation room, found that the front of the coil was frozen up but the back side wasn’t, called Jose he advised that they prop the door open to the meat cooler and it caused the coil to freeze up. I de iced the coil and the temperature started to drop. I checked out with manager. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99821
Sams Club 6619 7/15/2023 Peter Mejia Travel: 1200 Arrival: 1330 Departure: 2030 WO# 253771534 Arrived on-site for leaking case checked in with manager on site. Case leaking was medium temp case in online pick up area. Found damaged seals on some of the doors but managed to repair some of them, kinking in seals. Case was leaking from the top of the unit. Found drain evap pan not working and outlet reset was tripped. Pushed it reset button and tested float switch to ensure it was working, it was . Evap pan very dirty and hose clogged, vaccumed and cleaned evap pan and water tested to ensure it worked. Additionally, drain pan for evap coils were very dirty, pulled case and cleaned and vacuumed them. Water tested and no further leaks were found. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99834
8/1/2023 4:57:59 PM Cobian, Bernardo -0001 Arrived on site checked in with manger gained access to the rack house reset 3 compressors on rack A and reset 4 compressors on rack B compressors were locked out due to plumbing company shutting water off to repair a water leak on a pipe behind the rack house reset the compressors and made sure the temps went down job complete | Compressors/Motors | Compressors/Motors | 0.99662
7/26/2023 8:54:18 PM Paruleski, John -0001 Called out for ac in optical not working Met with manager Dahlia Inspected and found AC unit not running Checked all ops and found bad contactor Removed and replaced contactor. Got unit back online. Monitored and verified temps dropped. All ops check good | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.98696
8/1/2023 Jones, Makayla -0001 Checked out case. Took paneling off in the back. Found that floor drains are clogged for all of meat market . Plumber needs to come out. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
Time In: 1300 Time Out: 1530 LTA Receiver Float Switch Alarm (Home Office Automated Call) Receiver float switch alarm not present on arrival. Receiver at 15%, sight glass solid column, pressures at 9/264.p Leak checked the rack, and found a 5,000+ PPM leak on Comp 1 flare nut. Sprayed bubbles to confirm. Tightened but down and the leak was sealed. Added in 200# of R-407a into the rack. Receiver now at 60%. All cases at temp. Job Complete | Compressors/Motors | Compressors/Motors | 0.9963
Francisco V 8/11/23 Travel 2030 Start 2200 Departure 2330 Checked in and out with Marcus. On arrival found roll seal door stuck Cleaned sensors on the bottom and found the safety strap moved Reset safety strap and reset roll seal door. All ops okay job complete. Walmart app will not allow me to check in called to get checked in and out. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99728
Checked in with Heidi then began checking the cases. Found both S3C controllers were in comm loss. Cycled power to each unit then verified the sensors and transducers were reading correctly. The systems are running well but were alarming for high temp at the end of the defrosts due to the comm issues. Both systems are running well and are near setpoint. Checked out with Heidi, call complete. | Nuisance Calls | Nuisance Calls | 0.99833
7/18/2023 5:30:05 AM Franco, Ryan -0001 On site. Labor: 1100-1630 Diagnosed grounded exhaust motor and a defective TStat. TStat was sending 120V but could not sustain the load. Belt was also broken. Picked up parts and material. Replaced motor and belt. Set tension. Spliced wire in 1-gang box and ran conduit to new TStat. Tested all components. Motor pulling 5.2A/7.4A. Rotation normal. Thermostat set to 80°f per David. Job complete. | Compressors/Motors | Compressors/Motors | 0.99796
7/17/2023 1:43:04 PM Hanamornsate, Thirathanawat -0001 7/14/23 TH Time in: 10:00 Time out: 12:30 CS-12 HUSSMANN MN: IC2SM12 SN; MY18F044806 Arrived on site and checked in with Service channel and mod (Alex). Checked the location. Found case bad airflow. Take the product, Cover plates, Deck pans and shelves out. Closed the liquid line valve. Plugged out all fan plugs. Used bucket contain hot water and Deiced 3 Coils. Found drain pipe was slowly drained and flushed it by CO2. Cleaned drain pan. Put the plates back wall back. Plugged in all Fan plugs. Opened the liquid line valve. Put Deck pans, Cover plates and shelves back. Checked the temperature showed 32 degrees F. Cleaned work area. Informed and checked out with MOD(Brad) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
Travel: 09:00-11:30 Onsite: 11:30-14:30 Sn# Sam’s Club 6624 Sc# 230724-0467 Po# 251692338 System: RTU 17 -High Space Temp UPON ARRIVAL CHECKED IN WITH MOD AND SERVICE CHANNEL APP -RTU 17 ZONE TEMP WAS 81 -EVAPORATOR COIL AND COMPRESSOR WERE PARTIALLY ICED UP, DUE TO LOOSE BELT -ALLOWED RUN TIME TO DE-ICE COIL -PICKED UP 100FT OF WATER HOSE TO REACH CONDENSER COIL -CLEANED CONDENSER COIL: VERY DIRTY -TIGHTENED BELT AND RECORDED SPLIT -SUPPLY AT 56 -RETURN AT 82 -INFORMED MOD OF WORK PERFORMED AND OBTAINED A SIGNATURE BEFORE MY DEPARTURE. JOB COMPLETE. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99785
Travel: 1345 Time in: 1800 Time out: 2145 drove to shop. Picked up drain pan Drove to sams club Checked in with MOD Unwired drain heaters Assisted tech in changing out drain pan for MTB-9 Cleaned all ice Cleared drain pipe Rewired heaters Reassembled unit De-iced rest of ice in unit Turned unit unit into defrost and it was working correctly Drain pan clear and drain pipe Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9966
8/21/2023 6:21:45 AM Fuentes, Erick -0001 Job complete 8/14 Arrived onsite and checked in with management. Located temp sensor in optical doctors office which is labeled as rtu 2. Went up to roof and located rtu 2. Found the condenser fans running but the indoor fan and compressor was not. Began tracing out all high voltage and control voltage. Did not have 24v to fan or compressors, unit is not calling for cooling. Called sams monitoring and found that unit was tripped on air flow switch. Reset unit and began working properly. Checked airflow switch and is working properly and airflow is good. Checked pressures and monitored unit for normal operation. Went back down to dr office and checked temperatures and are dropping with good air flow. Will come back tomorrow to follow up on unit. 8/15 Arrived onsite and checked in with management. Went up to rtu on roof and found unit off called monitoring and got no answer. Went down stairs to doctors office and checked all temperatures. Unit was actually off on temp(satisfied). Went back upstairs to roof and waited for unit to come back on and checked pressures and for normal operation. Unit is working properly at the moment. | Nuisance Calls | Compressors/Motors | 0.99837
Arrived on site and checked in with manager mark. Mark directed me to the POs cooler and explained the lights have been out for the last week. Checked light switches to verify that lights weren’t turned off. Switches worked and went to look for ballast on the case. Wasn’t able to find it inside the case. Found junction box for the doors and lights. Opened up junction box and testing for voltage. No volts we’re coming from any of the circuits. Had a manager unlock the rack house and the electrical room. Began searching for the breakers for the circuit. Checked the electrical room looked for the breakers for the case. Went back to the rack house and began looking for breakers to the case. Found the breakers for the cooler door lights and began looking for a tripped breaker. No breakers were tripped. Went back inside and needed a scissor lift to get access to the top of the case. A second tech was called for safety. Once second tech came, brought second tech out to the floor to escort scissor lift to the top of the cooler. Once on top of the cooler. Began looking for ballast. Ballast couldn’t be found. Checked for voltage on top of the cooler. Opened up the junction box. Inspected wires leading down to the junction box down below. Had voltage of 115v. Power leading to the junction box inside the cooler had 0 v. inside the cooler. The piping leading to the junction box was forcefully ripped from the junction box and bent mid way through the piping. Second tech helped identify breaker responsible for power to junction box. Turned off breaker. Cleaned up area and secured all covers for junction boxes. Put scissor lift back. Updated manager Noel and chism. Checked out with manager Noel. Pushing to outside contractor. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99653
Checked in with service channel located asset tag. True self contained cooler in curbside running warm. Verified probes hooked up gauges checked condenser coil. Coil was dirty cleaned out checked evaporator fans. When diagnosing evaporator coil found the back of it iced up. Had to shut unit off overnight to clear ice on evaporator. Will have tech return following morning. Checked out with Veronica Luna and service channel. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99833
8/2/2023 Valdez, Paul -0001 After finishing previous call checked rack room found all compressor running and nothing in alarm walked the store and found a end cap Case read 75 degrees had meat department pull the case to save product pulled all shelves out and the the back panels found both Evaporator coils iced up closed the liquid line hand valve and unplugged the fans deuces the coils double checked both coils free of ice build up Opened the liquid line hand valve and plugged all fan fan came on put the back panels on and bottom shelves checked for air flow Had good air flow put all shelving back in the case and watched temps fall to required set points found no other issues job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99785
We arrived at the store, we checked with the manager, we went to the case and checked how it was running, the case is running at its regular temperature and everything is working well. | Nuisance Calls | Nuisance Calls | 0.99731
7/31/2023 Quezada, Arturo -0001 230731-0023 Answered phone call from dispatch Started route to Roswell Re-routed 7/31/2023 Ortega, Uriel -0002 GP#230731-0023 Drove to Roswell, NM Arrived at store and checked in with the store manager. Working on RTU#15 with no communication for pharmacy area. Found breaker off. Unit off due to a grounded compressor. Disconnected compressor harness and disable cooling. Fan only working. Communication back on unit. Ordered new compressor. Will return to install new compressor and re-enable cooling. 8/2/2023 Ortega, Uriel -0003 GP#230731-0023 Drove to Roswell, NM Arrived at store and check in with store manager. Working on RTU#15 pharmacy unit. Recovered all system refrigerant. Removed defective compressor. Installed new compressor with new filter drier and electrical harness. Charge unit with 410a refrigerant according to nameplate. Verified system pressures. Unit properly working. Job complete. | Compressors/Motors | Compressors/Motors | 0.9981
8/7/2023 6:30:41 PM St. Amant, Kenneth -0001 Sam club #: 4709 System: MTB-15 SC: 230807-0291 PO: 253157564 —————— 8/7/23 Kenneth St.Amant Checked in with manager Arrived on site checked in with location gained access. Took case apart and found the left fan unplugged So I took the back panel off to make sure it was not ice up Manager wanted one of the employee to clean the case really fast before I put it back together So once the employee was done cleaning the case I put the case back together and case it at 35° Checked out with manager Sonia Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99738
Arrived at location, checked in with manager Erik. Let him know I am here for leak detector box broken in pos cooler and is alarming. Manager Erik told me one of his associates bumped into leak detector box, that may have tripped it. Proceeded to check leak detector box to verify its not broken. Leak detector light is going off. Brought leak detector in and leak checked the store and pos cooler. No leaks detected in store. Went leak detector control box and cycled power to reset leak detector box. After I reset leak detector box. All leak detectors are in OK status and are running at normal operations. No alarms present. Cooler is at set point temperature and all cases are temping properly. Let manager Erik know the resolution and leak detector box is good to go and no leaks. POS Cooler Zone 3 leak detector box Brand: Emerson Model: MRLDS-250 Serial: 20082085 Checked out with manager Erik Call complete | Damage by Customer | Nuisance Calls | 0.66884
Sams 6683 Murray 1-17-23 Wo 230716-0279 Po 251007054 Compressor B2 Waiting Quote Travel 1745-1800 On job 1800-1930 Travel 1930-2000 Compressor Needed Carlyle Model 06CY665E-103 Serial 1321UE3571 Contactor needed Dp360240F Auxiliary Needed 1950243 3 gal mineral oil 200 Viscosity Needed Found compressor 1 tripped disconnect Found compressor 2 disconnect in off position Checked winding ok Checked short to ground non Found 460 at Contactor but L3 drawing 0amps Compressor single phasing B2 Shut off B2 at disconnect Left note for next tech Left B1 running amps ok Need to replace compressor B2 | Compressors/Motors | Compressors/Motors | 0.99853
7/31/2023 3:14:21 PM Ried, Nicholas -0001 Completed. Checked in with management. Checked controller and found temperatures reading approximately zero. Checked freezer and found no issues. The door must have been open for a long period of time. Found ice on fan guards. Removed ice and cleaned the area. | Nuisance Calls | Nuisance Calls | 0.99707
TT 2200-2230 Onsite 2230-2330 TT 2330-0000 At arrival checked into SC app and was allowed into store by John. Located bakery case not at temp. Bakery case middle section no airflow. Removed product, wire shelves and deck pans. Found evaporator fan motor non operational getting 115V. R/R motor. Fan back online, airflow restored. Temp at DA 36fdegs. Was allowed out by John. Unable to check out of SC app unable to verify case even when scanning QR code. Checked out via phone. Call complete. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.94845
7/21/2023 9:02:20 AM Moran, Greg -0001 Completed arrived and talked to manager. Took sizes of broken parts. Picked up new parts. Fixed both drains. One on C7 and one on C6. Let manager know the repair was completed. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99774
Arrived to location, checked in with Greg. Found circuits b05, b03a and b03b at setpoint of 28. Checked graph found graph spike at the same time management was conducting case cleaning. Management sent an email to Monitering stating they will be turning ball valves off at case in order to properly case clean. Ball valves were turned off, case was cleaned whilst happening temps spiked. Cases are now operating to standards and are at setpoint. This lineup will be cleaned every Sunday night due to it being fresh meat would recommend a note be put in for this store to avoid unnecessary calls being put in. Call completed, checked out with Greg. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99596
8/5/2023 10:59:10 AM Johnston, Andrew -0001 Checked in with Heidi then began checking system B11. B11a is not reading a temp at the thermometer and B11b is running at 45 degrees. Removed the S3c controllers from the case and found both had alarms. Reset B11a and monitored operation. The unit is cycling power every few minutes which is shutting down the solenoid and preventing both cases from running. Checked B11b and found the controller is running correctly. Swapped the two controllers to see if the system would run. B11a is now running consistently and maintaining setpoint while B11b is running but now showing a case temp. Will order a new S3c controller on Monday and install it as soon as possible. Checked out with Heidi, call incomplete. 8/7/2023 5:18:06 PM Johnston, Andrew -0002 Picked up the new controller and brought it to the store. Checked in with Heidi then began replacing the controller. Disconnected the bad controller then swapped all the wiring to the new one. Turned the new controller on then waited for the programming from the rack to download. Verified the parameters in the case then found both controllers were showing as B11b which was causing a network error. Attempted to change the programming but was unable to. Called Novar and Sporlan but neither was able to get in to the system to adjust the settings. Got the log in for the remote case controller then went in to the parameters and adjusted the case labels. Verified the comm wires were installed correctly then reset the IP address on each unit as they were showing the same. Both cases are now labeled correctly and running without issues. Monitored case operation to ensure they would both reach setpoint. Both cases are running well and maintaining setpoint. Checked out with Codee, call complete. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.92119
On-site 1200-1300 Arrived on site. Checked in with manager, Hellia. Made way to roof to check RackC comp3. Previous tech left a note and has diagnosed bad compressor. Spoke with previous tech and compressor has been ordered. duplicate | Compressors/Motors | Compressors/Motors | 0.99864
last week on first visit water was dripping from the case during defrost there was a slight bit of ice build up on the inside track but not in the pan I removed the ice and have them change the defrost settings came back today everything looks fine spent time on phone with tech support going over defrost parameters the case is now set to go through 6 defrosts per evaporator per day | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99687
Travel: 1800 Time in: 1900 Time out: 2130 checked in with MOD Located LTA-07A oand LTA-07B Cases had airflow Thermostat read cases are at 1 degrees and 2 degrees Product blocking means of service Had product removed Disassembled cases Used hose and hot water to de-ice cases and clear drain pans Plugged fans back in Fans working Reassembled cases Cases had good airflow and went back to temp Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99828
TT: 0600-0700 Onsite: 0700-1500 Lunch: 1100-1130 -Arrived on site checked in with MOD -located dairy walk in -Found that coil had frost and built up ice on C2b -when going into defrost water would drop on the floor -Proceeded to put C2b into defrost -Cleared ice with hot water making sure coil was free of all frost and ice -Noticed drain had blockage preventing proper flow of water to drain -cleared drain pipes making sure water flowed through properly. -after clearing drain and removing ice from coil made sure no other evaporators in dairy had ice build up -No other issues found -All fans in dairy working properly and running at proper temp -call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99863
Travel 1715 Arrival: 2030 Departure 2300 Checked in with Amanda Checked out with Amanda Reason for call: self contain high temping Unit: KYSOR WARREN Model: FX5SN -03RUN Serial: C17H00391 Upon arrival self contain was temping at 30 upon arrival Checked for air flow and ensured coil had no ice build up Temp thermometer was reading air flow at 29 Noticed dirty condenser coil Grabbed nitrogen and cleared condenser coil and fan Used meter to check amp draw -amp reading 5.1 Connected gauges to gather head pressure Head pressure while running was 260 Checked start capacitor with meter -Read at 80.6 micofarads -within proper operating range of 72-88 Monitored unit while checking operations unit continued to meet set point with out fail Checked wiring to ensure proper connection was being made Found no issues with unit Call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99728
7/29/2023 2:33:06 PM Gonzalez, Richard -0001 Gp230729-0082 1230-1530 ot Checked in with manger worked on BS6B island Wo252146338 Found coil iced up deiced coil and pumped down system cleaned screen also cleaned drain and made sure everything is working correctly case back to temperature showed manger | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99868
8/22/2023 6:12:01 AM Braswell, Caleb -0001 Inspected case and found evap drain pan full of water located drain line and cleared drain line with nitrogen tested with water and system drained normally no further issues at this time | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
Start time-1030 End time-1145 complete checked in with Oscar went to ice cream case A10A to check temps all temps are good (-8,-6,-4) came out of defrost home office call called walmart home office to check defrost schedule and set point temps set point10 defrost schedule-termination at 55 degrees or 45min. 1 defrost per day checked out with manager Oscar | Nuisance Calls | Nuisance Calls | 0.99834
MTB 2/3 Safety Poles Quote Time in 0730 Time out 1600 8/07/2023 Robert F Help technician Bob E repair safety poles. See Bob’s notes | Non-Mechanical Door Repairs | Damage by Customer | 0.75365
Start time-0045 End time-0115 follow up check in with manager Thomas A. Dodd II checked case B02a product pulled and coils iced up valve turned off manager leavening so I will have to come back tomorrow to de ice checked out with manager Thomas A. Dodd II | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99844
Jul 24, 2023 I found RTU off. Checked controls and wiring, found a short on the blower motor wire arching to ground. Repaired wiring and everything is working properly. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.99588
Arrived on site checked in with manager and service channel . Located coffin case 16.1a high temping at 36 . Removed product and found evap coil completely iced up . Shut off ball valve and let coil deice itself . Found drain pan clogged and icing up coil . Cleared trash and drain line . Will return tomorrow to turn circuit back on . No further issues . Follow up 0800-0945 travel 0945-1145 labor | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99862
Assisted tech with temporary repairs to drain pan. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99658
8/4/2023 Petty, Kevin -0001 Alarm went out at 1342 didn’t get alarm till 2100 Drove to store found system out of alarm. Also found compressor 3 off on high head pressure. Reset compressor and made sure all alarms clear . | Compressors/Motors | Compressors/Motors | 0.99848
8/2/2023 1:02:32 PM Canadas Garcia, Yelson -0001 I came and checked in with the store manager and checked the A2 compressor and found that it was protected by the oil switch, so I reset it and the oil pressure differential and suction pressure tests were done and it was within normal limits but the oil receiver was completely empty, so I went to buy the oil and the oil filter and I changed the oil filter and the receiver has two full sight glasses and it works inside normal | Compressors/Motors | Compressors/Motors | 0.99865
7-27 Scotty Sparks Travel time 0600-0730 On site 0730-1400 Departure 1400 Checked in and out with Kaytlen Found both POS WIF Needing strip curtains. Removed old strip curtains from both freezers. Installed 2 new sets of curtains. Job completed. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99602
8/27/2023 4:57:56 PM Ried, Nicholas -0001 Worked on refrigeration repairs as per PM quote. Incomplete. 8/31/2023 3:26:23 PM Ried, Nicholas -0002 Completed PM repairs as per quote | Misc. Billable Repairs and Service Calls | Compressors/Motors | 0.87692
8/8/2023 1:38:11 PM Corchado, Sergio -0001 Grocery freezer A5 A4 checked in with mod Found door was open Checked coils for iced build up Do to moisture build up Found iced build up on 2 Evap Forced several defrost Coils cleared up Waited for temps to drop Checked out with mod | Nuisance Calls | Nuisance Calls | 0.9977
Sam’s club #: 6619 System: cafe freezer SC: 230720-0317 PO: 251406123 —————— 7/21/23 Kenneth St.Amant Travel-09:00-10:00 Onsite-10:00-14:30 Checked in with manager Arrived on site checked in with location gained access. When to the cafe freezer and it was off When to the roof checked gas and psi and it was good To Look at the DEFROST TIME CLOCK and it was bad Put new DEFROST TIME CLOCK time in and the cooler kick on Put it in defrost to make sure it goes into defrost and comes out and it does Cooler is back running and good Checked out with manager Kelly Job completed | Nuisance Calls | Nuisance Calls | 0.99797
On site. Labor: 1300-1600 Checked EP2 for potential issues. Walked the roof to see which units were not producing condensation or not running. RTU #83 only had two circuits running. CK3&4 tripped on high head pressure. No issues with condenser fan start components. Condenser motors amp draws were all within normal range. High head pressure potentially a problem during extreme ambients. RTU #12: All condenser relays not receiving 24V. Found a loose common connection. Tested. All circuits running. AHU1 Munters unit lost power to T5 XFmer. Diagnosed a dirty smoke alarm. Cleaned out and all controls turned on. All circuits operating normally. Overall store temp was at 72°f. Adjusted front and south side store temp to 70°f. It is currently 110°f. Coil cleaning for all outdoor coils is recommended in the future to help with capacity loss during high ambients. This will help with low temperature splits. All RTUs and AHU are operating normally. Job complete. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.61995
7/19/2023 5:39:04 AM Rivera, David -0001 7/18/2023 David Rivera checked in found the door . Had condensate took door off checked voltage it was good. Cleaned the prongs and the door installed it back on . The door needs to be replaced the heaters are going out. Will send info to Willie to order parts. Job incomplete 9/8/2023 5:24:07 PM Arriaga, Luis -0003 On site had to locate crate finally we found it they had it hidden behind some other pallets waited for them to take out all the pallets located door that needed replacing and replaced it took old door outside along with the pallet it came in cleaned up area and checked out with Dan | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99356
-arrived on site. -found short on distribution block for rack 208vac power. -150amp breaker 208v breaker tripped. -breaker won’t reset now, it’s bad. -called bay power after hours and opened up store. -got the new breaker and returned to job site. -fitted and installed new breaker and electrical. -Daniel Blount is here for same issue but on a different ticket. -added eight 60 pound r744 cylinders to rack. -rack back operational and circuits pulled temp. -Daniel will keep his call open for a follow up to top of co2 levels up to 25% and order new distribution block. Bay power was not a vendor on our list of vendors when creating a mobile tech PO. Used the work order number as PO. Picture of invoice from bay power attached for breaker purchased. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.48769
Completed Checked in with manger on site went to meat prep room replaced fan guards no other issues found | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.461
0900-0930 travel 0930-1000 Called out for pharmacy AC too cold Met with manager Kim on arrival Inspected and found pharmacy cold at 68 Inspected unit and found unit running. Contacted Walmart home office and had temp setpoint changed from 71 to 73. Home office was reading a temp of 70 in the pharmacy, but could only bump up the temp 2 degrees. Monitored and verified temps increased slightly. All ops check good | Nuisance Calls | Nuisance Calls | 0.9982
Checked temperature and case was at setpoint temperature. Manager Payne told me to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.99777
7/16/2023 3:49:56 PM Cosgrove, Reese -0001 On-site 1930-2300 Arrived on site. Checked in with manager. Made way to MTB15 for rotisserie prep room Temp sitting at 50° Evap coil was frozen up One of the fans was not running Found it disconnected from plug, reconnected and fan turned on Deiced coil Monitored prep room and dropped to 40° Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9982
Arrived at the store, logged into Service Channel and spoke to the manager Stacy. I looked at A 6.1, A6.2 and all the bunkers and all temperatures are down to setpoints. With good cold airflow. I spoke to Stacy and told her what I did, and what I found. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99827
Time in 1730 Time out 1800 On site got a call for LTB comp 5 -found compressor not running -checked operations -found compressor bypassing -need to quote out compressor | Compressors/Motors | Compressors/Motors | 0.99857
Jul 21, 2023 I deiced 2 evaporator coils. I had tech support put it through defrost and check parameters, everything is operational. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99747
8/30/2023 Sovran, David -0001 Arrived on site and checked in with manager mark. Told to look for devin in charge of the meat department. Went to devin. Devin said there was a leak in the evaporator drain line above the meat cutter but it hasn’t happened in a week. Went to the meat prep room and looked at the evaporator fans were off in defrost. Waited to see if there was any leak on the unit since it was in defrost. Waited for the defrost to end without any leaks. Grabbed the ladder from the van and set it up underneath the evaporator coil and drain line. Grabbed a water measuring cup and filled cup up three times with water, pouring it to drain pan to recreate leak. No leaking. Repeated process again with another three cups of water. No leaking. Brought ladder out to van and checked out with manager mark. Call complete Model WK15GAC Serial TO8M03816 Heatcraft No asset tag or circuit indicator | Nuisance Calls | Case Cleaning/Deicing | 0.99793
7/17/2023 2:57:51 PM Alvarado, Christopher -0001 At site measure strip curtains sent info over to office to get ordered. 9/7/2023 9:08:08 AM Cochran, Lila -0002 Complete. Went to cafe, freezer asset tag did not match. Asset tag on ticket matches walk in cooler. Removed all old air curtains Replaced with new air curtains in both coolers. Checked out with manager Mhisani ford | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99618
Travel: 1700 Time in: 1930 Time out: 2030 Arrived at sams club Checked in with MOD Located case C-01a Turned off refrigerant valve Unplugged fans Disassembled case Product already removed from case Case was at temperature but had no airflow Ice on top of coil but not a lot Case really dirty Used water bucket and hose to clean coil and drain Plugged fans back in Reassembled case Turned refrigerant valve back on Case now has airflow and back to temp Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99574
Already on-site previous work order after check operation found the defrost schedule have two defrost per day instead four defrost per day. I call monitoring and fix the issues now case A9.4 and A9.5 have 4 defrost per day | Nuisance Calls | Nuisance Calls | 0.9984
7/23/2023 3:56:45 AM Monjaras, Daniel -0001 Checked in with manager Giovanni. All employees were about to leave when I arrived. I was able to check a few things before they left. Verified no iced coils. Verified fans are running. Went to rooftop to verify condenser is running. Receiver level is 35%. Manager mentioned to me that there is a compressor being ordered and that a tech told him that it can affect the temps a little bit. Verified only 3 comps are running. Coils are at 37 degrees. -C01 C02. Checked the other coils as well. Checked out with manager Giovanni. | Compressors/Motors | Nuisance Calls | 0.90587
01100-1300 2 hours reg time arrived on site, checked in with britany, found circuit A05 running warm in defrost, called novar found case defrost settings at every 6 hours for 65min, adjusted defrost to 45min every six hours with a 55 defrost temp termination in place. cleaned up work are and checked out with britany. | Nuisance Calls | Nuisance Calls | 0.99834
Sams 6683 Murray 8-8-23 Service call 230807-0541 Po 253175007 Something Fell Thru The Roof And Broke Something In The Cafe Freezer Like A Pipe Job complete TT/ST 1630-1730 ST 1730-1745 TT/ST 1745-1815 Returned to store Found box at -10° At temp System operating normal No more issues found Checked out with MOD Baily Sams 6683 Salt Lake 8-7-23 Wo 230807-0541 Po 253175007 Something Fell Thru The Roof And Broke Something In The Cafe Freezer Like A Pipe Follow up check Temps TT/OT 1815-2100 OT 2100-0015 Found freezer off 75° Found freezer full of water Found water dripping from ceiling and walls Found freezer and cooler sight glass flashing Found broken fire sprinkler went off in freezer Found water got inside EFM and shorted Found 1 leg of power missing from control circuit for fans Power cycled Unit Unit came back on Fans now on Replaced fan Used EFM D1125 fasco from Truck stock Leak checked w/ electronic sniffer no leaks found Used tape to tape up hole were fire sprinkler was removed Wiped water from ceiling and walls and squeegee water from floor Both fans came on Box dropped to 12° Went in defrost Store closing will return tomorrow to check temp Checked out with MOD Sébastien | Damage by Customer | Damage by Customer | 0.92805
Gp# 230720-0348 Time in 1630 Time out 2000 Hussmann M# F-8G S# MY21D037223 Checked in with manager George Located bunker case running warm at 38. Inspected it and found the coil was completely iced over. Contacted Sams EMS and requested manual defrost of the unit. Used sump pump, hot water, garden hose to defrost the coil completely. Once all the ice was removed, placed unit back into service. Defrost heaters and all fans are working properly. Coil superheat is normal. Unit is running normally at this time. Checked out with manager George. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99865
7/21/2023 2:14:48 PM Barajas, Armando -0001 Job completed. Informed management why I was on site. Located both freezers on site and looked into the ice building up. Found the freezer doors have metal rails that are welded onto the berms that surround the inside of the door. This are in the way of the strip curtains and not allowing them to lay flush against each other. This cause the air to enter the box when ever the door open. This will cause ice over time because you will build sweat on the metal frame. The right hand freezer(LTA3&4) also has a small gap on the bottom of the door. This is from missing concrete. Unless we cut that welded metal piece and level out the concrete and keep the employees from working with the doors open this will be a reoccurring issue. I was able to clear off the ice for now. Heaters on both doors are working properly as well. | Non-Mechanical Door Repairs | Case Cleaning/Deicing | 0.99749
7/31/2023 10:53:02 PM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Anderson MTC12 -All case high temp. Good air flow and no evaporator ice up -Suction/Discharge pressure reached set point pressure -Went up to the roof and receiver level at 60% confirmed this using torch -Compressor 2;3;&4 are toggle off. Compressors are in order according to previous tech. Waiting for compressor to come in -Request to removed products. Checked case filter drier and none are plug. -Case are cooling down and struggles after it come out of defrost. -Locate manager and talked to MOD Anderson and showed him what I did -Job complete. 8/2/2023 5:58:40 PM Hanamornsate, Thirathanawat -0002 8/2/23 TH TT: 7:30-9:15 Time in: 9:15 Time out: 13:30 Rack C Hillphoenix MN: PS SN: 110762-6 Checked in with Service channel and MOD(Anderson). Checked the location and found 4 cases started high temp. Found Suction pressure isn’t at set point. Checked pressure drop at Drier filter is good and no pressure drop. Checked Drier at cases are good. Checked the liquid levels is good. Found 3 Bad Compressors. Checked the History. It’s already to order parts in another work order (Refer PO#249406578). Will replace 3 Compressor in today. Informed and checked out with MOD (Anderson) and Service channel. Job finished | Compressors/Motors | Compressors/Motors | 0.99803
7/14/2023 10:41:10 PM Camacho, Javier -0001 Rack B Model: PS520VLRAD Serial: MA7935B 1-22-99 Checked in with MOD Rennel. Asked for machine room access. Asked for second tech for assistance with a ladder for safety reasons to get on top of the condenser and check CFMs. All fans working properly. Checked compressors, found 3 comps off on oil. Checked oil reservoir. Filled all the way to the top with oil. Checked oil filter. Filter had 100% pressure drop. Called supervisor, picked up new filter from supervisor to avoid opening parts house. Returned to store. Installed new filters. Opens up isolation valves. Oil began flowing to the compressors. Reservoir emptied out. Isolated and evacuated compressors to insure there was no liquid refrigerant before starting compressors. Once verified. Started comps one by one. Compressors started without issues. Suction pressure dropped to 24 PSI. Monitored temps. Sigh glass full. Temps on single digits and dropping at departure. Checked out with MOD Rennel. Call complete. 7/17/2023 9:36:30 AM Trevino, Salvador -0003 Help lead tech to with ladder to verified all ops on condenser coil due to condenser being on top of rack house | Compressors/Motors | Compressors/Motors | 0.99776
Job is complete Was at store for another call. Located rack B exterior of store. Pumped down compressor .Isolated compressor B1 and removed discharge thermal. Installed new thermal and evacuated compressor. De isolated and energized compressor. Monitor to make sure compressor running like normal. | Compressors/Motors | Compressors/Motors | 0.99857
7/28/2023 10:01:31 AM DeBeaulieau, Andrew -0001 Found bakery cooler C08 high temp. Superheat is 57degrees; frost line between screen and body. Pumped down circuit and cleaned screen. Returned circuit to Norma operation. Coil split 10degrees with 13 degrees superheat now. Box temp pulling down. Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99828
Job is not complete. Need to pick up new case controller and LCD screen from united refrigeration and return to install. Sensor was used from Nick M inventory. Please remove CDS valve from ticket and move to truck stock. Arrive to store and check in with manager. Locate case and found case running at temp. Begin checking ops and found case controller broken and possibly causing case to go in and out of temp. Also, did find sensor going in and out and reading off by 12 degrees. Replace sensor and case now reading proper temp. Will return to install. While on site found LCD for rack B inside of store not working. Contact novar and was told to replace LCD, will also pick up from united ref. All other cases are at temp at this time. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.93722
8/18/2023 5:31:33 PM Dodge, Chad -0001 Arrived at store found door latch not set right causing door to stay open and high temp Adjusted latch so door will close | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99718
Travel: 1115 Time in: 1200 Time out: 1700 checked in with MOD Located MTB5A+B Leak coming from fan Accessed scissor lift Turned off fans Removed insulation from drain pipe Disattached drain pan from drain pipe Used C02 and water to clear drain pipe Noticed drain pan to dirty to just use water to clean Removed entire drain pan Washed muck out of drain pan and used rags to clean Used scissor lift to housed drain pan back up and reassemble it Reconnected drain pipe to drain pan Reinsulated drain pipe Went to rack room to check defrost on unit and it was Noticed rack rack room and condesers dirty Cleaned rack room and condensers Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.98026
8/3/2023 4:58:36 PM Avila-Lara, Luis -0001 wIF 1.1-1.2 checked in with MOD Located WIF found evap 1.2 leaking water drain pan was hit with forklift bending the right side corner to pitch down causing water to drain from corner of the evaporator drain pan Got water melted ice from corner pushed drain pan up to level stoped leaking water down Found no other issues Job complete | Damage by Customer | Case Cleaning/Deicing | 0.9983
7/28/2023 5:14:15 AM Gary, Raymond -0001 7/28/23 Ray Gary Arrived onsite and checked in with the manager (Chasity)Went to compressor one and it was running Went thru some checks of my he compressor and found no issues I called Sams monitoring and spoke with(Trina)She verified that the compressor is not in oil Lärm THIS JOB IS COMPLETED | Compressors/Motors | Compressors/Motors | 0.99845
8/2/2023 4:06:58 AM Cosgrove, Reese -0001 on-site 2430-0230 Arrived on site. Made way to RackA. Found comp3 & comp1 not running Comp3 was not calling, comp1 was tripped on oil lock out Reset oil control for comp1, compressor is running and operating properly Checked gas and oil pressure, checks ok Checked pressure drop across filters, checks ok. Comp3 cycled on when calling to run All checks okay at this time Job complete | Compressors/Motors | Compressors/Motors | 0.99848
8/16/2023 Delgado, Fidencio -0001 Arrived on site checked in mod CARLOS and service Chanel. Proceed to Pharmacy tempnat 71 degrees registers little dirty. Got roof access found rtu20 supply 52 degrees filters just replaced 6-24-23. Went track to Pharmacy got ladder and cleaned all 4 supply registers. Just alittle dusty . No issues with ac and filters good normal lint on registers after yrs of not cleaning. Checked out mod CARLOS and service channel. JOB COMPLETE | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.98476
8/8/2023 4:48:28 AM Robak, Anthony -0001 Anthony Robak Checked in with MOD Jordan Went to case B5D and found it at temp Found who put the ticket in and they meant to put in MTB-11a and b Went to case MTB11 a and b and found it at temp Checked airflow and all cases had good airflow Went to rack B to check temps and found all four coils reaching setpoint of 31 degrees Went to case and used temp probe and showed management temps of each case All cases on B11A and b at temp Explained to management that product has to be behind airflow line or else product will not be at temp Went up to RTU 6 to check ops because of case humidity Found compressor 2 off on hhp Found bad fan capacitor and replaced with capacitor CR10X440 All condenser fans up and running Reset comp 2 and checked pressures First stage cooling now back online Checked AHU 1 ops which serves area that the case is in AHU is running properly The excess humidity in the case is due to general high humidity in the area Case is also next to meat and chicken prep area While on site, found compressor B5 off on oil safety Checked contactor and it checks out Oil safety working properly Reset compressor and checked oil pressure Oil pressure is same as crankcase pressure Compressor B5 needs oil pump replacement Will order oil pump for comp B5 Valved off compressor and left toggled off with note Checked out with Chelsea parts on order | Compressors/Motors | Compressors/Motors | 0.99853
Travel 1530 Start 1600 End 1930 Self contain unit running warm Checked in with MOD Located unit. Unit was 26°. Both Evap fans running.inspected condenser coil. Both coils dirty. Turned off unit Brushed coil clean used CO2 to clear dust out of coil. Inspected Evap coil lit ice on top of coil d-iced coil put case back turned unit back on unit at 30° Checked out with MOD CALL COMPLETE | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99715
7/18/2023 3:56:45 PM Caban, Nathan -0001 Checked in with Dutchess MTB 15 running high temp Found all 4 evaporators iced up, not draining water. Had store move product to gain access. Got spotters and moved scissor lift to cooler. Removed ice by isolating coils and running through defrosts. Could not use water due to product under coils, only got access to top shelf under coils. After insuring ice completely clear, blew out drain lines from inside cooler and then moved lift to outside of cooler and blew on each drain line from the outside as well. Each of them was stopped up with black sludge/debris. Drain pans were all in good shape, just build up inside the main drain. Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99864
7/19/2023 2:25:34 PM Perez, Secundino -0001 07/18/23ZP SAMS CLUB 4704 System A4 & A5 -Upon arrival check in with service channel. -Located the mod to check in. -Got access to the WIF. -Found the doors open as they are loading the box. -System had then went into a defrost on arrival -Waited for system to finish its defrost cycle. -System kicked on and waited for temps to drop. -Temps had dropped to 8F and then spiked up. -Went to the WIF found the reach in doors open as they are stocking product. -Graphed temps on the WIF, WIF drops below 2F when the doors are remaining closed. -System is operating normally. -Called home office and waited 20 minutes to get ahold of them. -Had them look at the programming for the WIF and had them change the refrigerant type from 448 to 404. -High temps are Due to heavy foot traffic and doors being left open while stocking. -Informed the mod of the situation -This call is now complete | Nuisance Calls | Nuisance Calls | 0.99835
Arrived on site and checked in with the manager. Went to the roof and started to going through the RTU’s and AHU’s and the units we couldn’t get on network. Put them on stand alone to get them cooling. AHU has a short that has to be located and RTU 13 control board screen is blank. Will have to order a control board for 13. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99587
Located case and it’s not in alarm it’s at set point 30 degrees. | Nuisance Calls | Nuisance Calls | 0.99671
1600-1630 lunch 1630-2030 travel OT 2030-2130 labor OT Arrived on site and checked in with manager Sandra Located bakery walk in cooler Found safety strap on the inside of door pulled and buckle was stuck on door Freed buckle and put strap back in place Using jog function on controller I put the door down. Made sure no error codes were present. Pushed open button to test. Door opened ok Tested door several times opening and closing it to make sure it functioned good Door working normally now Job complete Checked out with manager Sandra | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.79474
Completed. Checked in with management. Spoke with employees in Home Meal solutions. Waited for food prep to be completed and all food removed from the area. Removed old drain pan. Installed new pan. Installed fan guards and temp sensor. Cleaned unit. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99729
This is a duplicate call. 230820. Notes and time will be put towards that call | Nuisance Calls | Nuisance Calls | 0.99823
Sams 4730 West Jordan 7-25-23 Service call 230725-0155 Po 251763787 Cafe WIF 45° Job complete Travel 1200-1230 On job 1230-1315 Checked in with MOD Found WIF at 0° at arrival Found both Cafe boxes with doors not latched Ice build up from doors not being closed Shut doors Employee reopened doors and didnt close it behind them Looks like a combination of doors open after a defrost No other issues found unit at 1° but started a defrost 5 minutes ago | Nuisance Calls | Nuisance Calls | 0.98885
Time in 1430 Time out 1800 Call complete Arrived log into SC and check into MOD to remove and replace fans for VFD -picked up parts -got roof access -removed and replaced fans on rack A,B and D -check operations VFD now ramping and in drive MOD -call completion | Compressors/Motors | Compressors/Motors | 0.94024
7/30/2023 5:53:59 PM Toomer, Collin -0001 OT TT:17:00-19:00 OT:19:00-20:00 Arrived checked in with manager suman, proceeded to the rotisserie preparation room, found that the front of the coil was frozen up but the back side wasn’t, called Jose he advised that they prop the door open to the meat cooler and it caused the coil to freeze up. I de iced the coil and the temperature started to drop. I checked out with manager. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99827
Checked cases on cases A9.1 2 and 3 was running in low temp trouble shooting problems find to be the setting on controller was wrong Novar re down setting now cases are working correctly | Nuisance Calls | Nuisance Calls | 0.9983
8/7/2023 10:37:59 AM Robak, Anthony -0001 Anthony Robak Checked in with MOD Whitney Went to rack b for automated call all circuits high temping Circuits were high temping while rack b was shut down on to ticket 230804-0441 Checked all temps All circuits at temp Found compressor B3 off on oil pressure Checked contactor and oil safety switch All check out but found oil control running low Adjusted oil control until it maintained oil level All comps on B side running Rack suction at temp All circuits at temp Checked out with Whitney complete | Compressors/Motors | Compressors/Motors | 0.99847
TI:10:00 am TO: 12:00 pm Helped diagnose issue with Justin and Anthony, losses connection on unit on roof for cooler by Cafe, made sure that issue was fixed and cooler was coming down too temp | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.96122
0945-1200 travel Ot 1200-1330 Ot Called for walk in cafe cooler warm Met with manager Amanda on arrival Inspected cafe cooler found fans off and no refrigeration happening. Located a tripped breaker for C1 cafe cooler Reset and got unit back online Inspected condensing unit on rooftop, unit online and running, box is running 40psi, temp is dropping to below 40. All ops check good on departure | Nuisance Calls | Nuisance Calls | 0.99745
EnRoute: 18:15 Time In: 19:45 Time Out: 20:45 M: TD500-108-VC-4-FHSLF-B S: S18H00057 Home office stated that RACK B was moved over from Opus to Magnum, that’s what was causing the Comm loss issue. Due to the high ambient temps it’s causing high discharge and suction pressures but suction is fluctuating and within threshold range. Toggles on comp #1 to help with suction pressure. Home office stated that there is no comm loss issue. Waited about 45 minutes and suction dropped down to appropriate pressure. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.98472
8/2/23 TH TT: 7:30-9:15 Time in: 9:15 Time out: 13:30 Rack C Hillphoenix MN: PS SN: 110762-6 Checked in with Service channel and MOD(Anderson). Checked the location and found 4 cases started high temp. Found Suction pressure isn’t at set point. Checked pressure drop at Drier filter is good and no pressure drop. Checked Drier at cases are good. Checked the liquid levels is good. Found 3 Bad Compressors. Checked the History. It’s already to order parts in another work order (Refer PO#249406578). Will replace 3 Compressor in today. Informed and checked out with MOD (Anderson) and Service channel. Job finished | Compressors/Motors | Compressors/Motors | 0.99669
Currently in temp no issues found. I checked out with manager Shay | Nuisance Calls | Nuisance Calls | 0.998
Arrived on site checked in with store manager gained access to work area cafe walk-in cooler MTC-U1 walk-in was temping at 65 upon arrival went to roof inspection condensing unit and determined that compressor was going off on high head due to condenser fan motor not working went to parts house picked up new motor and replaced it turned unit back on motor operates properly with no issues walk-in cooler came back down to temp call complete | Compressors/Motors | Compressors/Motors | 0.99829
8/17/2023 8:01:05 PM Smith, Stephen -0001 EnRoute: 18:15 Time In: 19:45 Time Out: 20:45 M: TD500-108-VC-4-FHSLF-B S: S18H00057 Home office stated that RACK B was moved over from Opus to Magnum, that’s what was causing the Comm loss issue. Due to the high ambient temps it’s causing high discharge and suction pressures but suction is fluctuating and within threshold range. Toggles on comp #1 to help with suction pressure. Home office stated that there is no comm loss issue. Waited about 45 minutes and suction dropped down to appropriate pressure. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.95184
8/22/2023 1:03:14 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke with the manager Stacy. I looked at the walk-in freezers and all fans are working properly. I spoke to Stacy and told her what I found and what I did. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99809
Checked found ice building up in drain pipe found drain insulation found bad heater need to get pipe and drain heater de ice drain pipe due to drain heater not working found lose wire on wire nut pipe ice damage pipe repaired pipe repaired insulation tested deforest ok | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.94247
ST 1500-1730 Already on site for another wo Walked sales floor Found multiple bumpers track screws stripped Removed 1/4 self taping screws Installed 5/16 self taping screws Bumpers are now secure Walked sales floor with Erick Call complete | Non-Mechanical Door Repairs | Misc. Billable Repairs and Service Calls | 0.57791
Parts pick up 0800-0915 TT 0915-1030 On-site 1030-1215 Went to local vendors to pick up gaskets. Drove to store and checked in service channel and with manager. Put gaskets in sun to make them pliable, and take out the wrinkles. Replaced both door gaskets and verified they are sealing. Job complete. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98662
7/25/2023 6:42:22 PM Ruiz-Serafin, Alex -0001 Will need to quote and order parts Lennox: M# LGE060H4BH2G S# 5605F05889 Compressor: M# ZP54K3E-TFD-130 S# 05CD9044N Liquid line drier: C-163-S Contactor 3pl 40 amp 24v coil 12 lbs of R-410a Recovery charge, welding charge, electrical misc. 2 techs 8 hrs RTU 21 offices and server room-arrived onsite checked in with MOD received roof access located RTU found it with breaker trip ohm out blower motor, condenser motor and compressor and found compressor with open winding and system tested positive for acid will need to replaced compressor, liquid line drier, and contactor will also need to apply acid treatment 7/26/2023 9:12:11 PM Munoz, Julio -0003 Sams club 6235 Wo #230720-0350 Po#251411216 Rtu 21 -upon arrival to the store and I introduced myself with manager -I went to pick up parts for more information check Alex noticed 7/27/2023 7:06:47 AM Ruiz-Serafin, Alex -0002 RTU 21-arrived onsite checked in with MOD Todd received roof access located RTU r/r compressor liquid line drier and contactor checked weld with nitro then pulled vacuum pull 500 microns added 11.13oz of 410a started unit up then we found TXV not working properly had to recover refrigerant and removed and weld in a New TXV pressurize with Nitrogen check welds then we pull vacuum to 500 microns added the refrigerant that we had recovered RTU 21 back online delta T 20° split SC to compressor 20° coil temp 40° monitor server room temp and it’s at 72° offices down stairs are at 76° and still dropping Informed MOD of job performed and checked out | Compressors/Motors | Compressors/Motors | 0.99856
Start time-1730 End time-2345 arrive to assist with compressor change out | Compressors/Motors | Compressors/Motors | 0.99804
8/8/2023 9:27:36 PM Garcia, Adolfo -0001 MOD Ed -checked in with Ed and he informed me not to look at the snack bar freezer that the alarm was cas used by the door being left open too long -Ed directed me to the middle freezer and instructed me to focus on that -found that the door had been hit with a for lift and knocked off the track -the front end wheels were not on the track at all -sourced equipment form truck and retuned to get door on track -had to use prybar to slide it to the end were I could reposition the wheels and get it back on the track -once on the track I opened and closed it a few times -Cody MOD came and verfied it was working -found that it is missing the stoppers to keep the door from coming off track -Manufature is closed, will pass this on to CFS to get parts ordered to get the door its stoppers Checked out with Cody and let him know the WO will be in parts on order for now until we can source the parts. PARTS NEEDED Please Order two door stops please PN listed below. SYS Freezer #2 (middle) Asset Tag: 0052045 Brand: Regent KPS Model: n/a SN: DO.10046.2 Manufacture #: 800-826-3100 PN: 23-000822 Link: https://parts.kpsglobal.com/PublicStore/product/DOOR-OPEN-SIDE-STOP,284,153.aspx C.O. DIS: Breanna Placed in parts needed. 8/17/2023 6:33:33 AM Oleary, Holden -0002 Arrived on site and checked in with manager Luis. Had to wait to log in on service channel was on site at 0600. Looked over freezer door with issues and was not closing causing high temping freezer. Door is not able to close due to damage read over notes of last tech out for work order. POS Freezer 2 Asset Tag: 0052045 Brand: Regent KPS SN: DO.10046.2 Work was completed by general construction team on WO 230814-0233 TN 253683421. Pictures of completed work is on work order. Also went through the damage done to the POS cooler door WO 230804-0254 called dispatch and had call sent over to general construction while they are on site. Updated manager that POS freezers door has been repaired call is complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.93547
Returned to store. After getting tech support on the phone, tested inputs of compressor board and verified that the transducer will need replaced. Checked CIM board operation and inputs and found that the board is good but store will need to have remodeling company out to fix sensor issues as they pertain directly to the freezer they are working on. Checked out with manager and explained what is going on. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.97783
TT 1500-1600 Time in 1600 Time out 1730 Call complete Arrived log into service channel and check in with manager for LTA comp A5 -found compressor A5 off on high suction -got compressor back online -cleaned condenser -one fan is out and has been ordered -checked with dispatch fan has been delivered -will return tomorrow to remove and replace condenser motor on WO 230618-0178 | Compressors/Motors | Compressors/Motors | 0.99864
En Route: 07:30 Time In: 08:15 Time Out: 12:30 8.2A-8.3A high temping Checked in with manager and found fans not running due to case cleaning the night before, staff forgot to plug fans back in which caused the high temp alarms. Plugged fans back in and temps are currently dropping. Job is complete. | Nuisance Calls | Nuisance Calls | 0.98932
Tire Shop MUA -Arrived on site and checked in with store -found water line cracked on roof for swamp cooler -shut off water and repaired copper line -turned back on and confirmed proper float ops -job complete | Capital Replacement | Capital Replacement | 0.98476
8/10/23 TH TT: 13:30-13:45 Time in: 13:45 Time out: 17:00 RCU-1 Heatcraft MN: LLE170BEK SN: T17H00018 Arrived on site and Checked in with Service channel and MOD (Lesley). Checked the location. Found the Main drain pipe had gunks inside the pipe. Found Coil and Drain pan were dirty. Ran the water hoses. Turned off the unit. Cleaned the Coil. Dropped the drain pan down and cleaned it. Flushing drain pipe by CO2. Put it back. Turned the unit back on. Put a gallon of the water for test and no more leak water. Flushing main drain pipe by CO2 and checked it. No more gunks inside the pipe. Cleaned work area. Informed and checked out with MOD (Laura) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99632
8/3/2023 7:53:08 AM Fuentes, Erick -0001 Job complete Arrived onsite and checked in with management. Located cooler and found one fan out. Used lift onsite to access fans and found power wire shorted out and not making contact to motor. Once I fixed wire motor still did not come on. Took motor out and put case back together. Went to two different supply houses due to first one didn’t have it in stock. Once I had part returned to store and used lift to replace motor. Once replaced, turned power back on and monitored for normal operation. Motor is working properly, explained to management and checked out. | Compressors/Motors | Compressors/Motors | 0.99819
7/21/2023 4:44:24 PM Davila Garcia, Pedro -0001 Replaced door gasket and relocated defrost termination sensor | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99654
Upon arrival checked in with manager .. .located floral case and found conoressor not operating with power supply . Found start components bad . Replacedbwith new now up and running .also need to contact manufacturer to find out about flcprrect drain pan size . Once found out will order new for case . Let store know given condition of compressor that start components where bad that compressor might go out soon . | Compressors/Motors | Case Cleaning/Deicing | 0.91804
En Route: 1600 Time In: 1715 Time Out: 1815 C18a DT DELI High Discharge Air (Home Office Call) Checked into Service Channel Checked in w/MOD Jimmy Call is a duplicate. Located case, and it was at temp. Call was resolved 7/25. Fans were up plugged during a case cleaning. No further issues Checked out w/MOD Jimmy Checked out of Service Channel Job Complete | Nuisance Calls | Nuisance Calls | 0.99835
8/7/2023 4:24:42 AM Cosgrove, Reese -0001 On-site 1200-1300 Arrived on site. Checked in with manager, Hellia. Made way to roof to check RackC comp3. Previous tech left a note and has diagnosed bad compressor. Spoke with previous tech and compressor has been ordered on 230721-0032 / 251469647. Call complete. | Compressors/Motors | Compressors/Motors | 0.99848
8/16/2023 Jerry Mares GP# 230815-0298 0730-0830 TT 0830-1230 Onsite 1300-1430 Arrived onsite and checked in with Management. Located POS Cooler to check lighting issues club is having. Management said how there was 2 bright lights in the entrance of the cooler then goes dim towards the back. The lights were dirty, one light was completely out and another is flickering. Gained access to the scissor lift to get up to the lighting and checked each light. Cleaned off plastic covers and verified proper operation. Need to replace 2 LED drivers on 2 lights. Will order parts come back and replace. Pending Parts Philips LED Driver LED-INTA-1000C-60-DB | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99704
8/17/2023 5:30:38 PM Schrock, Kevin -0001 Checked in with manager when I arrived. Found A02 offline/in comm loss. Power cycled controls multiple times. Traced wiring and found punched comm wire and repaired section. Still unable to get back online. Spoke with Novar and followed procedures given by Novar team. After multiple resets of loop and modems, cases now back online. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.95324
GP#230801-0372 Checked in with store manager. Working on replacing 6x9 freezer door. Removed all forklift guards to access door. Uninstalled damaged door and took to warehouse. Unpacked new door at warehouse receiving area. Moved new door to walk-in freezer and installed. Mounted all hardware from old door. Door handle broken. Performed a temporary repair on handle. Need to order new door handle. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99687
8-15-2023 Adrian De La Cruz Jr GP# -230815-0298 PO# -253785111 0730 -0830 TT 0830 -1430 on-site Checked in with store manger. Spoke to the store managers to see the problems they were having. Located the walk in cooler I saw the concerns the store managers had about the walk in cooler. It was different shades of lights in there. The father you went down the walk in the more dim the lights got. I assisted my Lead tech for the rest of the job. Discovered we need to order a Balice control box. -follow up needed for parts -job complete | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.88915
Call being complete on 253232301 Per Corey, the module is being replaced on another work order. Case is operational | Capital Replacement | Nuisance Calls | 0.94908
Food court Walk-in cooler heat craft model SME054VE serial number D05L16422 Was already on site. Unit disconnect was off walk-in box was above 60 F product was removed. Power unit on. Compressor Short cycling found run capacitor has failed. Remove and replace with same type check start capacitor check refrigerant. pump compressor down. Verify condensing unit is working. Box is now at set point . This call is completed. Parts used 15 MFD capacitor | Compressors/Motors | Compressors/Motors | 0.98221
Arrived on site checked in with manager (Mike) and service channel . Located B06a ice cream case . Cases on arrival at -5 . Found no issues with cases . No ice build up all fans running . Good airflow . Checked door gaskets and door tension to make sure they close properly. Found no issues . Case was either being stocked with product or customers left door open . Case temp on departure-5 . No further issues . Job complete 1000-1030 travel OT 1030-1130 labor OT | Nuisance Calls | Nuisance Calls | 0.99764
Picked up the new controller and brought it to the store. Checked in with Heidi then began replacing the controller. Disconnected the bad controller then swapped all the wiring to the new one. Turned the new controller on then waited for the programming from the rack to download. Verified the parameters in the case then found both controllers were showing as B11b which was causing a network error. Attempted to change the programming but was unable to. Called Novar and Sporlan but neither was able to get in to the system to adjust the settings. Got the log in for the remote case controller then went in to the parameters and adjusted the case labels. Verified the comm wires were installed correctly then reset the IP address on each unit as they were showing the same. Both cases are now labeled correctly and running without issues. Monitored case operation to ensure they would both reach setpoint. Both cases are running well and maintaining setpoint. Checked out with Codee, call complete. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.46982
07/26/23 Anthony DeCarlo Travel 1315 Arrival 1400 Departure 1700 Awp proair M#CR43-0616-051 S#021550844-3 Checked in with mod and service channel on arrival Went to gas station hut A/c unit. Found breaker off at panel. Verified return coil has extensive fin damage causing restriction. Switched on, unit is running but not blowing cool air Opened up a/c panel verified comp receiving power. Checked starting components and caps are well within spec Checked safeties, all are closed. Checked Tstat, verified closed calling for cool Checked windings found within spec Power cycled unit multiple times, hearing a clicking coming within compressor. Verified comp is over amping over 40amp and cutting out power. Internal overload is too weak Unit it’s out dated with r22 charge. Quote to replace old unit with 120v ductless mini split unit. Call incomplete Checked out with mod analisia and service channel on departure | Capital Replacement | Capital Replacement | 0.59489
In 15:00 out 18:30 Gp#230717-0455 Checked in with manager Working on rack B system B10 high temping Checked case and found case had all fans running and no ice build up Continued troubleshooting case and found sensor had fallen into corner of case Relocated sensor and checked controller Also cleaned honeycombs on case Sensor is now reading much better and running at temp 35 degrees No other issues found at this time job completed | Case Cleaning/Deicing | Nuisance Calls | 0.9981
8/14/2023 3:40:19 PM Braswell, Caleb -0001 Arrived at location case b05 seems to be reading normal temperature setpoint 28 case temp 27.9 case b03 a and b are running warm with low airflow tried to run system through 2 defrosts had small effect will return in morning before store opens to de ice coils 9/28-BILL INCURRED. THIS CALL IS COMPLETE IN SERVICE CHANNEL. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99221
Onsite 1830-2030 MTB compressor 4 lockout -Arrived onsite checked in with MOD Todd received motor room access located rack b and found compressor off on oil pressure reset OFC checked NOP monitored compressor did a capacity check on compressor all checks out good informed MOD of job performed and checked out | Compressors/Motors | Compressors/Motors | 0.99852
Arrived at the store logged into Service Channel and spoke with the manager, Antonio. I looked at the bakery door and the bottom track mount was crooked. Stopping the door from opening. I adjusted the mount and re-secured it. So now the door opens smoothly. I spoke to Antonio and told him what I did and what I found. This is complete no need for follow up. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.87457
1245-1300 travel 1300-1600 Called out for ac in optical not working Met with manager Dahlia Inspected and found AC unit not running Checked all ops and found bad contactor Removed and replaced contactor. Got unit back online. Monitored and verified temps dropped. All ops check good | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.98987
Cody warden 7/15/23 Travel-1400 Arrival-1430 Departure-1700 Checked in with manager/ Daniel Responding to A/c unit not cooling at fuel station. Lennox M/N XC13 -018 -230 -01 SIN 5807C21774 Checked thermostat and verified it was calling and working properly. Found condenser fan not running. Checked breakers to ensure they weren’t tripped and checked pressures. Pressures were good. Inspected condenser coils and found them severely plugged Cleaned coils with pressure washer and coil cleaner. Hit high pressure switch on condenser unit and unit came on and started cooling Checked out with mod/ Daniel Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99524
Roll Seal Model #: SC-325 Serial #: 0005222 Call for roll door for W/I A1/A2 getting stuck/not closing. Arrived and checked in with manager. Located W/I and inspected. Roll Seal controller giving “EOF1” error code. Error code for Encoder Signal Lost. Contacted Shane with Roll Seal for tech support. Flipped motor safety bar back into proper position. Found emergency cord had been pulled out too far. Re-inserted emergency cord back into position. Reset controller. Opened door fully to set parameters. Closed door fully. Door now opening and closing properly. Cleaned work area. Checked out with manager. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9971
7/31/2023 5:59:46 PM Hernandez, Rodrigo -0001 LTA 8 Bakery FRZ Arrived checked in with mod for bakery WIF high temp On arrival freezer at 25-30F Found coils frosted up due to roll seal door not closing Ran a defrost cycle on freezer to remove all ice and clear coils Verified heaters are operating and fans are shutting off in defrost Ice build up issue is door being stuck open Cleared coils and pulled door down to maintain freezer temp (Door repair on another WO that I will address after this WO) Freezer down to temp and out of alarm Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9985
7/26/2023 11:07:29 AM Brooks, Byron -0001 Travel: 0830 Time in: 0945 Time out: 1045 Arrived at sams club Checked in with MOD Located walk in cooler next to pharmacy Issue is with acorn system which we can’t fix Did walk through cooler to check for any water leak Did not find water leak Let manager know Checked out with MOD | Nuisance Calls | Nuisance Calls | 0.99767
8/10/2023 7:20:01 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke with the manager Justin. I looked at the sliding freezer door and found that the upper wheel bearings that slide in the track are broken and not rolling properly and need to be replaced. Also the handle on the door is missing a bolt and a plate so the handle needs to be replaced. I was then told there’s a second door that is off the track and needs to be fixed. Looking at the bakery freezer I found that the floor track is missing and the door is not sliding properly. I will order all parts needed and leave this work order open and return when the parts come in. I spoke to Justin and told him what I did and what I found. 10/4/2023 5:43:57 PM Zaun, Paul -0002 10-4-23 Paul Z -FU to install handle and door guide bakery Freezer LTA6 check in with manny found Bakery freezer not sealing added door guide by drilling into concrete and adding 3/8 lag bolt removed door from rail to get door guide in place tighten nuts on lag bolts door handle is not bent handle was hit with forklift SS end cap separated from door SS end cap is twisted and not repairable bolts are severed in door and had to be tapped out -one not removable added spacer to bring out kick plate adjusted door and replaced missing parts Manny pointed out they have an extra door verified it was a freezer door and size is 6x9 door opening is 6x9 asked manger to put a call in to install door that’s on site job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99661
8/15/2023 4:29:29 PM Garreans, David -0001 Time in 1630 Time out 1800 Checked in with manager Jonathan. This compressor locked out on high pressure when sprinkler was not under condenser. Turned sprinkler back on and reset compressor. Monitored operation, compressor is now staying running. Checked out with manager Jonathan. Racks A M# TC500-085-SL-4-NVF-A S# 0202001182 Tg# 0054076 Complete | Compressors/Motors | Compressors/Motors | 0.99855
8/3/2023 La Cava, William -0002 8/3/23 Sams 4735 230803-0319 252761476 Arrived and checked in to service channel and manager. Working with tech Robert F. Assisting him with door repairs see his report for details. Complete 8/3/2023Frietze, Robert -0001 Curbside 3 door cooler On the right 8/03/2023 Robert F Bill L Already onsite checked into ivr and with mod. Accessed curbside pickup and 2nd cooler has last door on the right has broken hinges. Called to get second tech to drop door and remove broken hinges. Fished out bottom hinge stuck inside door. Then installed bottom and top hinges and adjusted torque for proper closing. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99697
Checked in with manager when I arrived. Found A02 offline/in comm loss. Power cycled controls multiple times. Traced wiring and found punched comm wire and repaired section. Still unable to get back online. Spoke with Novar and followed procedures given by Novar team. After multiple resets of loop and modems, cases now back online. | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.97061
Completed. Checked in with management. Used scissor lift to access the evaporators in the meat walk-in. Found drain pans dry but cleared lines anyway. The evaps did have condensation. Wiped off all water. The condensation is mostly due the fact that there are no strip curtains on the main door allowing moisture into the cooler. Management has already placed an order for new curtains and hardware. Unable to use Service Channel to close ticket. Confirmation number 658424316 | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99531
Found both LTA1 coils starting/ are iced up. Found heater switch in “ON” position but no power. Knowing that I’ve ran into other Walmart/Sams stores wired backwards, I switch them to OFF and the power restored to the heaters. Ran it through three defrosts. Will send someone back tomorrow to see whether then need manual defrosting (probably a little at least) or if they can catch up. Temps are good in box when systems are on. Not complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99813
Time in 1700 Time out 1800 Check in with manager for compressor B5 -found compressor running -called home office they said compressor has no faults | Nuisance Calls | Compressors/Motors | 0.998
8/12/2023 10:13:18 PM Medina, Alexis -0001 8/12/23 Sam’s club 6613 Rack MTC Comp4 Oil Lockout Alex Medina arrived on site, checked in on IVR and MOD Hector. Obtained roof access for rack MTC. Headed to rack. Confirmed comp 4 off on oil on controller. All other comp SG half full and running. Checked comp 4 oil SG and found it to be half full. SG had a mixture of yellow and white indicating possible liquid in comp. Isolated compressor and pumped out liquid from comp. Opened comp up and ensured SG filled up. Cleared alarm for comp 4 and started it up. Comp making a loud humming noise. Clamped up and comp is pulling 166 amps. Comp is locked up and will need to be replaced. Will need to get compressor under warranty. Rack suction high @ 480# with a setpoint of 427#. Did a store walk around and found that cases under rack C are in the low-to-mid 30’s. Cases maintaining temp for the time being. Informed MOD hector. CALL NOT COMPLETE, COMP 4 NEEDS TO BE REPLACED. 8/23/2023 6:57:28 PM Flores, Jose -0003 Rack C compressor 4 New Bitzer Comp Model #: 4FTE-20-2NU-00 Serial #: 2504713763 Follow up to replace Bitzer comp. Used crane to bring down old comp and bring up new compressor. Left old compressor at Sam’s club to return for warranty. Suction pressure reaching setpoint now. CALL COMPLETE 8/23/2023 7:24:52 PM Martin, Rogelio -0004 8/23/23 RM Assisted lead technician on compressor change out | Compressors/Motors | Compressors/Motors | 0.99819
TT:6:30-11:45 ST:11:45-14:30 with lunch OT:14:30-18:00 OT TT:18:00-21:15 Arrived checked in with Mathew Gained access to the motor room. Assisted lead tech with compressor change on Rack B. Compressor #5. M:PS S/N:59210-3 After installed compressor we leak checked and started compressor. The compressor isn’t coming on called David and ran some test. Chris M. Called Jonathan and he advised put in for follow up and they will return next week. Call incomplete Needs follow up Checked out with Mathew. | Compressors/Motors | Compressors/Motors | 0.99865
In 08:00 out Gp#230808-0373 Checked in with manager Lucas Working on ice cream door with broken glass Case Model#ARMZC30 Serial#0508-102674INA Contacted Anthony doors and got glass door ordered Ordered door under Sam’s account using po#253260654 No ETA available at this time Order reference#01038981 Contact information 18007720900 follow up required | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99659
7/19/2023 5:06:29 PM Boscan, Adrian -0001 arrived at the store I checked the case and it was running hot, I looked for the condenser unit on the roof, I checked the unit and had the switch contactor burned, the contactor was changed and the equipment was under observation, the container was cooling to its regular temperature | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.99782
Arrive onsite and checked in with service channel and MOD Cathy LTA 5 SD Meat HussMann M# F-12G S# MY18H064791 -Checked air flow, low air flow -Request removed all product. Found evaporator fan motor not working due main power plug loose -Grab trash can and water pump. De iced coil -Run defrost and heat element reads 5amps -Monitor case temperature and reached temperature set point of 32f -Locate a manager and talked to MOD Hilda -Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99856
8/2/2023 7:11:26 PM Alcaraz, Jose -0001 Time in 1700 Time out 1800 Check in with manager for compressor B5 -found compressor running -called home office they said compressor has no faults | Compressors/Motors | Compressors/Motors | 0.99857
Sams 8177 -Checked in with manager upon arrival. -Located case listed on work order. Found no ice build up, management advised the work order had been completed a couple weeks ago. They stated that they had a walk in freezer leaking water. Ltb5b was leaking water onto floor due to condensation pan missing screw and hanging. -Remounted pan and inserted screw. -Pan no longer leaking. -Call complete | Nuisance Calls | Nuisance Calls | 0.99802
Complete Checked with manager Located produce walk in cooler Installed new one | Capital Replacement | Nuisance Calls | 0.99544
Gp# 230819-0001 Jesús Monreal 08/28/23 1200-1330 Rs Check in with mod Check alarm on compressor rack A follow up on the alarm check compressors for properly operation no more alarms compressor rack working properly all temperatures at set point complete | Compressors/Motors | Compressors/Motors | 0.9985
7/28/2023 3:25:21 PM Hanamornsate, Thirathanawat -0001 7/28/23 TH Time in: 16:30 Time out: 17:00 MTC-1 Heatcraft MN: WKE270BEC SN: T18H02102 Arrived on site and Checked in with Service channel and MOD(Hilda). This call is duplicated call. Reference PO#251495817. Informed and checked out with MOD(Hilda) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99843
Travel:0530 Arrival: 0700 Departure: Hvac unit : Cafe Brand: Lennox Model:LCB060HN2G Serial:5602E02629 Original Compressor: Model: ZR57K3E -TFD-830 Checked in with mod Rob Checked our with mod Vanessa and Irene Reason for call: Cafe running warm. Issue found: compressor grounded. Resolution: replaced compressor, TXV, Filter Drier, and add new refrigerant R407c will need to follow up finish call. Checked in with mod Rob and informed him that roof access was needed Roof hatch was unlocked and proceed to cafe unit Upon inspection of unit found it not running Checked disconnect -Good Flipped the breaker on and heard the indoor blower motor turn on After 10 mins the compressor contactor kicked on and immediately tripped the breaker Proceeded to check resistance on the compressor Found that compressor was grounded Spoke with mod about getting replacement Mod approved Proceeded to call supply shops Found compressor and proceeded to gather materials needed for compressor change out Contacted The crane company for crane truck Crane truck said they will send one to our location Proceeded to Supply shop to gather materials Crane did not arrive on scheduled time and informed us they will not be able to make Canceled crane and proceeded to lift compressor on to roof top along with tools and materials that were needed removed previous compressor, filter drier and TXV. Added new compressor filter drier and the supply shop had sent wrong TXV -proceeded to supply shop to pick up the correct TXV and proceeded back to job site Added acid away to compressor Pressure tested And held nitrogen Vacuumed until 420 microns Could not finish installation due to rain and wind headed our way. Will follow up on call Saturday July 22. | Compressors/Motors | Compressors/Motors | 0.99853
7/14/2023 7:40:15 PM Richardson, Preston -0001 Self contain unit running warm Checked in with MOD Located unit. Unit was 26°. Both Evap fans running.inspected condenser coil. Both coils dirty. Turned off unit Brushed coil clean used CO2 to clear dust out of coil. Inspected Evap coil lit ice on top of coil d-iced coil put case back turned unit back on unit at 30° Checked out with MOD CALL COMPLETE | Misc. Billable Repairs and Service Calls | Case Cleaning/Deicing | 0.99699
7/31/2023 6:30:31 PM Rudnick, Bryan -0001 Arrived at location, checked in with manager Mark. Proceeded to work on drain pan that is hanging in the walk in cooler that a forklift driver knocked off the evaporator. Took drain pan and straightened it back to normal as best as it can. Need to put new pipe fitting in because the old pipe fitting cracked from fork lift driver. Brazed in the new p trap fitting and put everything back together. Cleared all the condensation ice off of the coil. Drain pan is good to go. Let manager Mark know the resolution. Brand: Heatcraft Model: BMA245AWMSIA Serial: D00L04205 Checked out with manager Mark Call complete | Damage by Customer | Damage by Customer | 0.66691
Arrived on site checked in with manger gained access to the rack house reset 3 compressors on rack A and reset 4 compressors on rack B compressors were locked out due to plumbing company shutting water off to repair a water leak on a pipe behind the rack house reset the compressors and made sure the temps went down job complete | Compressors/Motors | Compressors/Motors | 0.99699
Checked in with manager when I arrived. Found rack B not reading suction pressure and compressors in fault. After getting in touch with tech support, a manual input of 25psi was set on the rack and 3 of the 5 compressors manually shutdown. Also found CIM41 board offline. Could not get board back online and will have to follow up on Monday as Novar tech support is not available until then. Checked out with manager on duty and explained what was found. | Compressors/Motors | Compressors/Motors | 0.99832
7/21/2023 10:29:47 PM Hanamornsate, Thirathanawat -0001 7/21/23 TH TT: 22:30-23:00 Time in: 23:00 Time out: 24:00 LTA-1 & LTA-2: Rollseal Door MN:6421-2283/ RS-500 Track Kit SN: 0009113 Checked in with Service channel and MOD(Melanie). Checked the location and found the Rollseal Door wasn’t all the way closed because the bad Door. It’s controlled by manual mode for now and already order the new Rollseal door with another work order. Checked the Manual operation. It’s working good. Keep to close all the way and temp going down but it not at temp. Needed to keep the door closing longer but the MOD(Melanie) not approve now because they want loading stuff from truck to the POS box. Informed and checked out with MOD (Melanie) and Service channel. Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99629
7/25/2023 6:23:42 AM Brooks, Byron -0001 Travel: 1700 Time in: 1930 Time out: 2030 Arrived at sams club Checked in with MOD Located case C-01a Turned off refrigerant valve Unplugged fans Disassembled case Product already removed from case Case was at temperature but had no airflow Ice on top of coil but not a lot Case really dirty Used water bucket and hose to clean coil and drain Plugged fans back in Reassembled case Turned refrigerant valve back on Case now has airflow and back to temp Checked out with MOD Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99532
TTOT 2130-2230 Time in 2230 Time out 2330 Rack A M# RNSX-D8-L064-M045-V4XLA-A S# S16H00036 Tg# 0050160 Checked in with manager Damien. Curcuits A10, A13 and A14 cases were all empty and liquid line hand valved off. Turned back on and all curcuits dropped back down to temperature. Manager on duty Damien has no clue why they were hand valved off. There was no ice and cases had good airflow. Checked out with manager Damien. Complete | Nuisance Calls | Case Cleaning/Deicing | 0.97401
8/19/2023 Hall, Warren -0001 8/19/23 arrived on site and checked I. With Rosemary the MOD. Went to rack room and verified all compressors are on line and checked case temperature. Went to walk in and verified that cooler was back at temperature. Found MTB-5 evaporator pan knocked loose due to product being lifted too high with forklift causing screw in back to dislodge. Reattached drain pan in correct position. This will complete this work order. | Damage by Customer | Case Cleaning/Deicing | 0.99623
8/3/2023 6:13:39 PM Upchurch, Keith -0001 Time in 0900 time out 1530 Arrives on-site checked in with manager went to roof found unit cooling. Called monitoring and they showed temperature in office was 77 set at 74. Washed condenser coils. Checked evaporator and was a little dirty. Brushed off evaporator. Turned unit back on. Unit started cooling. Watch temp come down. Zone temp is at 73 degrees call complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.997
TT 0900-0930 Onsite 0930-1830 At arrival checked into SC app and with Michelle. Assisted with R/R 4 CFM on rack B. See Mario A. Notes for further details. Call complete. | Compressors/Motors | Compressors/Motors | 0.97997
8/17 Tech William Placed in Service Channel Turned freezer back on and observed it come down to temp. Verified more info on hinge that is needed for proper door closing. Ordering Parts from United Refrigeration 8/14 Tech William Placed in Service Channel I replaced a fan motor on a self contained case. I had to source a motor locally so I had to go to several parts houses. I assisted Kody with troubleshooting and diagnosing the neighboring self contained case. We check electrical connections, safety switches, refrigerant levels and pressures. We determined that the case will need a new compressor. Kody is ordering one. | Misc. Billable Repairs and Service Calls | Compressors/Motors | 0.99565
8/14/23 TH TT: 7:30-9:00 Time in: 9:00 Time out: 10:00 MTD 4.1-B: HUSSMANN MN: IC2SM8 SN: MY20B11524 Checked in with Service channel and MOD(Joe). Checked the location. Cases is running at temp and good airflow. Checked the both Coils are running at temp and no iced up the plate back wall. Checked both graph temp are good. Checked the History and Found its duplicated call with WO# 230813-0084. Informed and checked out with MOD (Joe) and Service channel. Job Finished | Nuisance Calls | Case Cleaning/Deicing | 0.94955
7/18/2023 6:23:16 PM Dankenbring, Jarod -0001 Duplicate call see wo 230718-0335 | Nuisance Calls | Nuisance Calls | 0.99783
EnRoute: 8:00 Time In: 9:00 Time Out:11:15 Ticket was a duplicate ticket due to the emergency call this AM | Nuisance Calls | Nuisance Calls | 0.99821
8/16/2023 8:07:49 PM Garreans, David -0001 Time in 2100 Time out 2115 Checked in with manager Benny. Hussmann M# RGD-30D-72H-4-S/C S# 1030514201836193 The case is a self contained case and compressor was not running. Checked wiring and found loose wire that came off start relay. Put wire back on and compressor turned on. Case temperature dropped. Cleaned Honeycomb and condenser coil and case is now cycling off and off properly. Checked out with manager Benny. Complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99556
8/9/2023 8:55:20 AM Enciso, Juan -0001 call is the same as TN: 253288619WO#230809-0031 Checked in with Erik, went ahead and walked through the store, all the cases are good on temps, on cases C05 a and B, looked to be at 35 degrees, came outside to the rack house and checked the Sporlan control and the temps its showing is 35 and 30 degrees. I checked all systems on rack C, everything is on temp ranging from 28-32 degrees. Talked to Erik and checked out. | Nuisance Calls | Nuisance Calls | 0.99837
Returned to location installed new AC motor drive control after installation had to reset door parameters after resetting verified operation of door no further issues | Non-Mechanical Door Repairs | Compressors/Motors | 0.44808
8/9/2023 3:34:11 PM Maldonado, Chris -0001 Start time-0845 End time-1500 complete checked in with manager Sabine pulled product pulled case apart to find broken fan, coils iced up turned the valve off to defrost went to united for new fan put new fan in and finished de-iceing checked out with manager Sabine | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
Arrived at the store, logged into Service Channel and spoke with the manager Justin. I looked at the sliding freezer door and found that the upper wheel bearings that slide in the track are broken and not rolling properly and need to be replaced. Also the handle on the door is missing a bolt and a plate so the handle needs to be replaced. I was then told there’s a second door that is off the track and needs to be fixed. Looking at the bakery freezer I found that the floor track is missing and the door is not sliding properly. I will order all parts needed and leave this work order open and return when the parts come in. I spoke to Justin and told him what I did and what I found. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98667
Sama 6685 Provo 9-18-23 Service call 230819-0186 Po 254173718 Club pick up door wont shut Job complete ST 1845-2000 Shift 2000-2115 TT/SHIFT 2115-2145 Returned to store with parts Replaced door holders Replaced door tensioners Replaced door gaskets Replaced missing hardware Checked out with MOD Jeff | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99651
Arrived on site checked in went to rack house and found the rack down I tested for power and had power to the rack I went checked pressures rack was good hit the reset button on the head pressure and no luck I reset the boards and rack came back online I noticed the head pressure would rise real quick checked the condenser fan motors and they were running backwards I turned off the vfd and check for programming errors all working properly the rack had gone out on head pressure due to fans rotation waited till cases came down to temp and no alarms present checked out | Compressors/Motors | Compressors/Motors | 0.99816
8/3/2023 6:46:53 PM Fenton, Typhan -0001 Make: KYSOR/Warren Model: TD600-073-VL-4-FHSRX-A Serial: 1112000167 Unit: Rack A comp#4 -upon arrival compressor was off but the rack at suction set point. -I checked the compressor and the oil level was low. The reason for the low oil level is that the OLC needed to be adjusted. -I monitored system and OLC is satisfied and oil level was restored. No other issues system operational. | Compressors/Motors | Compressors/Motors | 0.99816
Marcos Caraballo 07-27-23 Travel 1630 Arrival 1730 Departure 1945 Meat prep C6A and C6B At arrival checked in with store manager Located meet prep high temping Began, deicing, frozen coils After all ice was cleared Went up to rack to check perameters Found that the system had no defrost cycle scheduled Spoke with Home office they were not able to set parameters for defrost Technician to follow up in the morning to set parameters/speak with novar systems This call is not complete Temperatures at departure, 46° Checked out and obtain signature from manager Kiahnah | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99833
7/20/2023 Bob and Robert LTA-7 Bakery walk in freezer back door On arrival tech check in with service channel and store manager. Helped Robert repair sliding door. Also repaired bottom floor guide and replaced broken floor stay roller. Also repaired torn down strip curtains with new brackets and 3 new strip curtains. Door now working properly and sealing properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99708
This is for Dairy walk-in cooler. Not Produce walk-in. Manager Mark specified that this call is for Dairy and has a different call he’s opening for Produce. On-site, checked in with manager Mark. Proceeded to work on Dairy cooler. Brought scissor lift over and connected hoses. Three coils iced up and leaking. Verified drains were clogged and iced over. Deiced all 3 coils and used nitrogen to clear out drains. Water is properly draining down drains now and no more leaks. Cleaned up everything and Let manager Nimah know the resolution. Dairy cooler C8 Brand: Heatcraft Model: WK270BEC Serial: T20F20531 Refrigerant: R407A C9 Brand: Heatcraft Model: WK270BEC Serial: T20F20535 Refrigerant: R407A C12 Brand: Heatcraft Model: WK270BEC Serial: T20F20533 Refrigerant: R407A Checked out with manager Nimah Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99838
15:15 pm -20:15 (5 hours REG) Arrived on site, checked in with MOD. Accessed the rack house and found on Rack A compressor 2 and 4 were off due to high head pressure. Checked controller and pressures were reading over 275. Went up top to condenser unit and found 1 motor not spinning due to blown fuse. Replaced fuse, but after doing so it tripped all of the condensor fans. After that we turned off all comps and shut off Rack A. Ran hose and took off fan shields. Sprayed water and cleaned thoroughly. Then sprayed from bottom of condensor. Put everything back together and turned on compressors. Head pressure dropped and comps are running. Will return with fuses and possibly new condensor motor. | Compressors/Motors | Compressors/Motors | 0.99812
7/18/2023 12:49:28 AM Monjaras, Daniel -0001 Checked in with manager Nate. Located WIF bakery. A08. Found emergency pull down was pulled. Rolled it back up. Tried to closed. Door was still having issues on closing. Found that the Service Cycles was blinking. Read into manual and needed to be reset since it reached its limit. Reset parameters. Verified door opens and closes. Monitored and tested a few times before departure. Checked out with manager Nate. | Non-Mechanical Door Repairs | Damage by Customer | 0.96021
8/4/23 Ray Gary Arrived onsite and checked in with the manager (Corey)Found the case not refrigerating The fans were on So I went thru my diagnostics and found the liquid line ball valve was closed off On Monday I believe I went and defrosted that whole case So I know it was working fine and the ball valve was in the open position There is construction going on so someone from that side my have actually shut the valve off I let the case temp out for a while and Called Sams Monitoring and spoke with (Ietta)She confirmed the case was out of alarm and working properly THIS JOB IS COMPLETED | Damage by Customer | Damage by Customer | 0.98494
Removed all damage broken hinge. Installed new hinge from van stock. Talked with Andrea showed her progress. Job complete.cleaned off graffiti from door | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99186
8/17/2023 7:15:49 PM SMITH, ANTHONY -0002 Accessed the rack house and found on Rack A compressor 2 and 4 were off due to high head pressure. Checked controller and pressures were reading over 275. Went up top to condenser unit and found 1 motor not spinning due to blown fuse. Replaced fuse, but after doing so it tripped all of the condensor fans. After that we turned off all comps and shut off Rack A. Ran hose and took off fan shields. Sprayed water and cleaned thoroughly. Then sprayed from bottom of condensor. Put everything back together and turned on compressors. Head pressure dropped and comps are running. Will return with fuses and possibly new condensor motor. 9/6/2023 10:39:16 AM LONCASTY, SEAN -0003 Returned and replaced condenser fan motor. Replaced all three fuses, now up and running. | Compressors/Motors | Compressors/Motors | 0.99785
8/5/2023 8:00:10 PM Andrews, Jacob -0001 Checked in with MOD and got roof access. Located frozen door LTA A1A and found case at -3. Checked surrounding cases all running at similar temps. Checked controller on roof and saw no alarms for case and graph looked normal. Called home office to see if they had anything different, no difference found. Checked out with MOD. | Nuisance Calls | Nuisance Calls | 0.99792
Head pressure running 325psi found water coil dirty washed coils monitoring, pressure running a at 305 psi on the day time temperature outside 103f will added a water sprinkler due to high out side temps in installed new sprinkler and hoses to help keep head pressure down due to high temps | Misc. Billable Repairs and Service Calls | Case Cleaning/Deicing | 0.99663
8/21/2023 1:55:57 PM Coffee, Nashanne -0001 Currently in temp no issues found. I checked out with manager Shay | Nuisance Calls | Nuisance Calls | 0.84506
8/20/2023 1:15:20 PM Hanamornsate, Thirathanawat -0001 8/20/23 TH TT: 9:30-10:15 Time in: 10:15 Time out: 12:30 Rack C Heatcraft MN: TD400-033-VC-4-OHD-C SN: S17E00058 Checked in with Service channel and MOD(Javin). Checked the Rack C and Found no power supply to the Rack C. Found Main Breaker of Rack C was tripped from Compressor 1. Checked shortage at Compressor 1 is good and no shortage with ground. Found Bad Contractor and Breaker Comp1 was trip. Removed bad Contractor out and Installed new Contractor and Auxiliary switch in place. Connected all electrical wires. Reset Breaker at the Rack C and Breaker of Comp1. Rack C come back to working. Checked all cases and Produce CLR temperatures. They are good temperature and no alarm high temp present now. Cleaned work area. Informed and checked out with MOD (Leandra) and Service channel. Job Finished | Compressors/Motors | Compressors/Motors | 0.99853
7/17/23 TH TT: 18:00-18:45 Time in: 18:45 Time out: 20:45 Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643 Checked in with Service channel and MOD(Justin). Checked the Rack A and found all Compressor were cut out from high pressure and Condenser Fan weren’t work. Found the LCD monitor fault. Reset the Controller. Turned on the VFD to by pass mode. All Compressor are come back to working. Found the Condenser Coil was dirty. Ran the water hoses and cleaned it. Checked the Suction pressure showed 12 psi and Discharge pressure showed 280 psi. Tried to turn the VFD to VFD mode but it isn’t working on VFD mode. Turned VFD to by pass mode for now. Checked all cases temperature. They are good temp and no alarm present. Cleaned work area. Informed and checked out with MOD (Justin) and Service channel. Job not finish Neededq follow up for High level tech to diagnose the VFD operation. | Compressors/Motors | Compressors/Motors | 0.99854
10-4-23 Paul Z -FU to install handle and door guide bakery Freezer LTA6 check in with manny found Bakery freezer not sealing added door guide by drilling into concrete and adding 3/8 lag bolt removed door from rail to get door guide in place tighten nuts on lag bolts door handle is not bent handle was hit with forklift SS end cap separated from door SS end cap is twisted and not repairable bolts are severed in door and had to be tapped out -one not removable added spacer to bring out kick plate adjusted door and replaced missing parts Manny pointed out they have an extra door verified it was a freezer door and size is 6x9 door opening is 6x9 asked manger to put a call in to install door that’s on site job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99502
Time in 1630 Time out 1800 Checked in with manager Jonathan. This compressor locked out on high pressure when sprinkler was not under condenser. Turned sprinkler back on and reset compressor. Monitored operation, compressor is now staying running. Checked out with manager Jonathan. Racks A M# TC500-085-SL-4-NVF-A S# 0202001182 Tg# 0054076 Complete | Compressors/Motors | Compressors/Motors | 0.9986
07/26/2023-Glenn Sr. and Bob E. Upon arrival checked in with manager and Service Chammel. Proceeded to Bakery freezer door. Assisted Bob on installing door gasket and foam filler. See Bobs notes. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99638
7/24/2023 5:54:51 PM Alcaraz, Jose -0001 Time in 1730 Time out 1830 Quote to clean coils Log into service channel and check in with manager for dairy WIC leaking water -found case at temp -inspected coils -coils have heavy debris and need to be cleaned -quote to clean coils 2 techs 8 hours each 10/11/2023 9:48:59 AM Toomer, Collin -0002 ST:11:30-11:45 Arrived checked in with Bryon Advised this call was completed. 10/9 This work was completed on WO: 231005-0268, and the produce cooler will be done on that work order as well. 10/29 by me and another tech. Call complete on this one Checked out with Andrea. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99796
arrived at the store I checked the case and it was running hot, I looked for the condenser unit on the roof, I checked the unit and had the switch contactor burned, the contactor was changed and the equipment was under observation, the container was cooling to its regular temperature | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.99817
8/15/2023 3:53:14 PM Arriaga, Luis -0001 Follow up needed 8-17 Arrived on site checked in found rack reading at 0 percent at time I pumped down the rack and it was low I went and leak checked down stairs on the cases and had the store assist in checking above the coolers and found nothing I then went back up to the rack and started to leak check I found compressor number 2 leaking from the liquid injection line pictures attached I went and ahead and valved compressor off and when I went to loosed the fittings I was able to just twist it off w my hand I put some leaklock and turned the compressor back on its no longer leaking will return and check to see liq level checked out with Cody 8/17/2023 7:31:57 AM Arriaga, Luis -0003 Returned to site checked receiver level its good conducted another leak check returned unused refrigerant added a total of 100 lbs of 407a checked out | Compressors/Motors | Compressors/Motors | 0.9983
Alarm went out at 1342 didn’t get alarm till 2100 Drove to store found system out of alarm. Also found compressor 3 off on high head pressure. Reset compressor and made sure all alarms clear . | Compressors/Motors | Compressors/Motors | 0.9984
7/16/2023 7:41:34 PM Johnston, Andrew -0001 Hussmann Model: RL-3 Serial: My12A000832 System: LTB-7C Checked in with manager then began checking the RIFF case. System B7c was temping high. Checked the coil for ice buildup and verified the fans were running. Checked the txv and found it was frosting at the body which can indicate there is a restriction in the screen. Pumped the system down and swapped the txv screen for a new one then turned the system back on. Went to the motor room and began checking the rack. Found compressors 2 and 3 were off on oil failure which was causing issues with the suction pressure. Verified the compressors had oil in them then reset them both and verified operation. Checked voltage and amp draw for each compressor then gauged up to the compressors and checked oil pressure. Both compressors are showing 70-80psi net oil pressure. Checked the oil reservoir and found it had 2 balls floating. Monitored rack operation and waited for the system to drop to temp. The case quickly dropped below 0 and is running well. Checked out with manager, call complete. | Compressors/Motors | Compressors/Motors | 0.99826
7/28/2023 5:11:35 PM Hanamornsate, Thirathanawat -0001 7/28/23 TH Time in: 17:00 Time out: 18:00 LTA-4: DT CFN HUSSMANN MN: F-8G SN: MY18H064792 Arrived on site and checked in with Service channel and MOD (Hilda). Checked the case is good airflow. Checked the temperature sensor showed -12 degrees F and no alarm present. Checked graph temp is good. Found the system was loss Communication. Fixed it. It’s on line and No found issues and no alarm present. Informed and checked out with MOD (Anderson) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99842
7/24/2023 3:22:25 PM Paruleski, John -0001 Called out for meat case B06a warm Met with manager Jen Inspected and found case iced up Had product pulled, shut hand valve off. F/u in AM to restart. 7/25/2023 12:59:06 PM Paruleski, John -0002 Called out to restart meat case that was warm Met with manager Dahlia on arrival Inspected and found unit completely defrosted. Restarted and monitored. Waited for case to drop to temp and initiated defrost. Heaters are energized. All ops check good on departure | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99838
8/10/2023 12:29:28 PM BURNS, DAVID -0001 Found Start components failed. Replaced start components and cleaned condenser. Everything is working properly. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.96441
Time in 1800 Time out 1900 Call complete Log into service change and check in with manager for C16b freezing product -case is running at set point of 22 -called home office and had the change set point to 30 degrees per manager request | Nuisance Calls | Nuisance Calls | 0.99838
Rack C compressor 2 and 3 alarm comp L/O . Compressors off on oil. Compressor oil levels ok. Reset oil controll. Both compressors operating ok 19amps each. Contacters ok. Check OLC k1, inspect clean glass. Tighten both oil controls. Rack oil level, oil filters ok. Cases at temperature. | Compressors/Motors | Compressors/Motors | 0.9986
8/22/2023 8:41:34 AM Stuart, Christopher -0001 Time in: 1030 Time Out: 1045 LTA 02 POS Freezer High Temp (H.O. Automated Call) Gained access to LTA Rack. LTA A02 reading -2 degrees. Not sure what caused extreme high temp. No issues found. | Nuisance Calls | Nuisance Calls | 0.98722
8/9/2023 5:53:18 PM Paruleski, John -0001 Called out for BS11 comm loss Met with manager Gio Inspected and found case online and working. Spoke to home office who said case was in comm loss. Was transferred to novar Spoke to Novar and novar could not connect to rack controller. F/u to contact Novar again to diagnose issues with case 9/22/2023 3:18:10 PM Nichols, Cooper -0002 Cooper Nichols 9/22/22 Duplicate call Completed already Reference call # 230920-0297 | Nuisance Calls | Nuisance Calls | 0.9982
TTOT 1800-1900 Time in 1900 Time out 2130 Checked in with manager Payne. Rack A M# RNSX-D8-L064-M045-V4XLA-A S# S16H00036 TG# 0050160 The entire rack A / AS was down. All compressors locked out and overheating. I valved off every compressor and started 1 compressor up at a time. All compressors have oil, are running and holding good suction pressure. Discharge pressure with all compressors calling is at 260 psi. All circuits out of alarm. Checked out with manager Payne. Complete | Compressors/Motors | Compressors/Motors | 0.99862
7/17/2023 Garcia, Rene -0001 Checked walk-in cooler at cafe/snack bar and found stuck head master(head pressure control valve). I had to bypass it and install a mechanical head pressure control. I had to recover the refrigerant front the system, remove the head master and install the new control and wire the condenser fan motor to it. I pulled a vacuum on the system and charged with refrigerant. Added 20lbs of R404A refrigerant. No other problems were found. | Compressors/Motors | Compressors/Motors | 0.99695
Rack B Kysor warren Model -TD430-098-SC-4-FXSRGBI Serial -0305001075 Checked in with manager kris on arrival. Call placed for compressor L/O on rack B. Went to rack house and checked ops. Found rack B maintaining suction at 55# Found all compressors online / no compressors found locked out . All systems are down to temp / no active alarms. Called home office and spoke with Zach. Ensured no alarms on there end and confessors are online. Job complete | Nuisance Calls | Nuisance Calls | 0.9953
7/17/2023 7:11:36 PM Hanamornsate, Thirathanawat -0001 7/17/23 TH TT: 18:00-18:45 Time in: 18:45 Time out: 20:45 Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643 Checked in with Service channel and MOD(Justin). Checked the Rack A and found all Compressor were cut out from high pressure and Condenser Fan weren’t work. Found the LCD monitor fault. Reset the Controller. Turned on the VFD to by pass mode. All Compressor are come back to working. Found the Condenser Coil was dirty. Ran the water hoses and cleaned it. Checked the Suction pressure showed 12 psi and Discharge pressure showed 280 psi. Tried to turn the VFD to VFD mode but it isn’t working on VFD mode. Turned VFD to by pass mode for now. Checked all cases temperature. They are good temp and no alarm present. Cleaned work area. Informed and checked out with MOD (Justin) and Service channel. Job not finish Need follow up for High level tech to diagnose the VFD operation. 11/10/2023 4:59:42 PM Simmons, John -0002 TTST 1300-1400 On-site 1400-1730 Checked in with manager on arrival Checked Rack A VFD. Rack A Kysor//Warren MN: TD400-054-SL-4-OHDL-A SN: 0603000643. Checked and reconnect vfd. Restarted and check and found the vfd working normally and found the cooling fan bad checked rack C&D vfd in bypass they also have hbad cooling fans. I will order cooling fans the vfds were turned off during during the summer. Parts on order. Fan assembly’s for danfoss vfd. Incomplete parts order 1/3/2024 5:01:20 PM Limas, Jonathan -0004 01/03/2024 Jonathan G Labor 1430-1800 Checked in/out: Kristen Multiple racks’ VFD assisted teck 1/3/2024 6:47:45 PM Alcaraz, Jose -0003 Time in 1430 Time out 1800 Call complete Arrived log into SC and check into MOD to remove and replace fans for VFD -picked up parts -got roof access -removed and replaced fans on rack A,B and D -check operations VFD now ramping and in drive MOD -call completion | Compressors/Motors | Compressors/Motors | 0.99858
7/25/2023 11:42:17 PM DeBeaulieau, Andrew -0001 Upon arrival found large oil stain and puddle outside Rack B side of motor room. Found Compressor B2 has leak on oil line to oil regulator line. Isolated and attempted repair with copper gasket; did not fix. Ordered new parts, leak section is isolated from rack. Cleaning up oil spill from leak while parts are enroute. Replace elbow between oil regulator inlet and angle valve on oil line. Used nylog and copper crush gasket to insure leak free seal. Check fitting with leak detector and confirmed repair complete. No other leaks detected at this time for Rack B. | Compressors/Motors | Compressors/Motors | 0.99855
Called out for rack B down. Upon arrival found rack SB down. Compressor #3 had tripped breaker. Compressor megged ok, reset and checked ops. Everything checked out good. Compressor #2 kept tripping on OFC. (it’s a rebuilt compressor). Swapped out legs (L1&L2) to change the oil pump rotation. Compressor stays on running and NOP @28#. | Compressors/Motors | Compressors/Motors | 0.99848
Jun 06, 2023 POS freezer. Found both heaters bad and 2 gaskets missing, as well as rear facer on bottom of door. Will call manufacturer in am to obtain and order parts. Jul 18, 2023 Took freezer door off POS freezer. Installed new heaters and gaskets, installed door. We are missing a leg of power, will need to come back and further diagnose. Door is now back on freezer. Jul 19, 2023 Checked on Freezer door and noticed it fell off the track. Adjusted the door so it can properly seal. Noticed the heaters on the door were not working. Found neutral butted by itself. Re-wired it into the other wires for door and it started to work. Door is working well. When removing electrical found tripped braker, unable to find due to employees wanted to leave. Will return to find missing leg of power. Rehung door. Returned and located braker. Found loose neutral in main electrical box. Corrected, now power not cutting in and out. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99684
8/17/2023 7:18:10 PM Homan, Timothy -0001 Nobody knew what this call was about and cases are at temp. Completing out. | Nuisance Calls | Nuisance Calls | 0.85692
GP#230731-0023 0500-0900 TT 0900-1230 RT 1300-1930 RT Drove to Roswell, NM Arrived at store and check in with store manager. Working on RTU#15 pharmacy unit. Recovered all system refrigerant. Removed defective compressor. Installed new compressor with new filter drier and electrical harness. Charge unit with 410a refrigerant according to nameplate. Verified system pressures. Unit properly working. Job complete. | Compressors/Motors | Compressors/Motors | 0.99808
Cooper Nichols 8/18/23 Travel 0515 Arrival 0715 Depart 1115 Arrived for suction # alarm Rack BS Rack running @ 52# on arrival with no alarm present Adjusted sub cooler EPR and Txv’s Now subcooling solenoids are shutting down & subcooling is achieving temp. When subcooler solenoids shut down rack BS suction # drops to now low 40’s from 52#. No alarms @ departure | Nuisance Calls | Compressors/Motors | 0.89393
John DiCecco 7-22-23 Travel 0730 Arrive 0800 Depart 1415 RTU 3 LCB060HN2G 5602E02629 Arrived and investigated newly installed compressor. Found terminals to be destroyed and insulation to be grounded with megohm meter. Recovered charge and removed compressor. Replaced filter drier. Pressure tested system and evacuated. Charged with 12# store stock of 407C. Monitored system operation and noted high suction pressure due to 95 return temp. Will return later in the week to verify pressures and ops. Amp draws stable and within range. Call incomplete. | Compressors/Motors | Compressors/Motors | 0.99711
Checked in with manager and was told the damage was repaired by the plumbing company’s electrician. Verified the systems were running well then checked out with manager, call complete. | Damage by Customer | Damage by Customer | 0.95558
7/20/2023 5:33:37 PM Frietze, Robert -0001 Bakery Freezer Door Strip Curtain Damaged LTA-7 7/20/2023 Robert F Bob E Upon arrival checked into ivr and with mod. Accessed back freezer door with tools. Found door top track with rollers crooked and bolts loose. Strip curtain header ripped off and missing three curtains. Used ladder to remove door from top track and rail. Had to go to part vendor to get new bolts and hardware that were damaged. Removed set screws on both ends of rollers to move inside of track further and square roller assembly to bar. Then installed new bolts and hardware to roller rail. Then reinstalled back into top rail. Used crowbar to lift door on each side to install mounting bolts into door on both sides. Adjusted nuts for proper height and that gaskets seal to jamb properly. Cut bottom damaged anchors in track and rotor hammered track into right position with two new concrete anchors. Then used grinder to cut anchors off of damaged and rusted stay roller. Then rotor hammered new anchors into new stay roller and adjusted to door. Removed damaged strip curtain header and installed new header pieces and installed three new curtains and cut to size. Job complete. 7/20/2023 7:05:13 PM Emmer, Bob -0002 7/20/2023 Bob and Robert LTA-7 Bakery walk in freezer back door On arrival tech check in with service channel and store manager. Helped Robert repair sliding door. Also repaired bottom floor guide and replaced broken floor stay roller. Also repaired torn down strip curtains with new brackets and 3 new strip curtains. Door now working properly and sealing properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99628
Travel: 1730 Time in: 1830 Time out: 2230 Rack B Model: PS520VLRAD Serial: MA7935B 1-22-99 Checked in with MOD Rennel. Asked for machine room access. Asked for second tech for assistance with a ladder for safety reasons to get on top of the condenser and check CFMs. All fans working properly. Checked compressors, found 3 comps off on oil. Checked oil reservoir. Filled all the way to the top with oil. Checked oil filter. Filter had 100% pressure drop. Called supervisor, picked up new filter from supervisor to avoid opening parts house. Returned to store. Installed new filters. Opens up isolation valves. Oil began flowing to the compressors. Reservoir emptied out. Isolated and evacuated compressors to insure there was no liquid refrigerant before starting compressors. Once verified. Started comps one by one. Compressors started without issues. Suction pressure dropped to 24 PSI. Monitored temps. Sigh glass full. Temps on single digits and dropping at departure. Checked out with MOD Rennel. Call complete. | Compressors/Motors | Compressors/Motors | 0.99788
Arrived on location checked in with the receiving manager and gained access to the roof top once up to the roof top I disconnected every unit from the backnet and set all units to run as a stand alone unit and verified all set points for heating and cooling ran each unit in test mode and cycled power once done I double checked each unit to verify they where all running and then checked each area the units supply air to to verify the employees are noticing the difference to ensure everything is running properly once complete I cleaned up the roof top and checked out with the manager I also informed him the initial issue has an open work order that has parts ordered for this issue as of now no units are communicating with novar through backnet this work order is complete and is in relation to Customers PO# 249522736 251843464 251682915 The calls are all the same issue and will need closed | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.60244
TT 2000-2100 Time in 2100 Time out 2230 Follow up Arrived log into service channel and check in with manager for multiple cases high temp -check rack found B6 a,b in alarm -no other alarms -found cases B6 a,b ice up -had product pulled -the store is closing soon and there is no over night crew -turn cases off to deice over night -follow up for tomorrow to turn cases back on and diagnose | Case Cleaning/Deicing | Nuisance Calls | 0.99653
Return to site check in with manager. Mike was shown case aso6 not maintain proper temperature replace CDS valve on as05 will return and follow up. This call is not complete Parts used CDST-4 | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.93398
arrival:1600 Departure 1745 Checked in with Anthony Checked out with Anthony RTU 16 Brand: Lennox Model: LGE060HH1G Serial: 5603G05645 Reason for call: RTU 16 Office A/C running warm Upon inspection of unit found unit to be off Proceeded to check for power at the unit Found power and disconnect to meet specs Initiated cooling using Tool called jumper king Cooling went to effect Called home office Home office said that hvac for job site is unavailable Proceeded to electric room down stairs near office Found RTU device reader Found Rtu 16 in comm loss Proceeded back up stairs and reset novar control board Cleaned board with brush to get rid of dirt debris build up Plugged everything back in and unit was now online Proceeded back to office Office was now cooling down and no longer running warm | Nuisance Calls | Nuisance Calls | 0.99788
0900-01100 2 hours reg time arrived on site. checked in with Wendy. found meat prep room evaporator fans filled with water , cleared drain line with Co2, clear water runs through drain and all good. cleaned up work are and checked out with Wendy | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
8/14/23 Cory Saenz Arrived on site checked in with manager picked up 8 60 pound drums of CO2 charged system with 480 pounds Co2 assisted one on new breaker install system back up and running. Will need to return to pick up CO2 cylinder. Temps coming down system back up and running. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.91434
8/5/2023 8:45:31 PM Haddad, Masoud -0001 Arrived on site checked in with the manager -checked A02 and A05 walk in freezers -found it’s at 7 degrees and 4 degrees -checked the evaporators and fans all fans are running -found some heavy frost on the evaporators -checked the receiver level and it’s good -checked high and low pressure and it was good -put A01, A02 and A05 on a defrost and after the defrost the temperature dropped to -1 -put on manual defrost again and all the frost on the evaporators melted and the temperature dropped again to -1 All checked good -call completed | Case Cleaning/Deicing | Misc. Billable Repairs and Service Calls | 0.51501
Job Complete Had to pick up parts for this job Arrived on site and replaced all of Strip Curtains in the Bakery Cooler. Job also required a fan motor replacement in the Bakery cooler but it seems to be working fine | Misc. Billable Repairs and Service Calls | Non-Mechanical Door Repairs | 0.98046
8/2/2023 7:24:13 PM Alcaraz, Jose -0001 Time in 1800 Time out 1900 Call complete Log into service change and check in with manager for C16b freezing product -case is running at set point of 22 -called home office and had the change set point to 30 degrees per manager request | Nuisance Calls | Nuisance Calls | 0.99831
7/24/2023 7:07:46 PM Soria, Rafael -0001 Arrived on site and checked in, went to hearing center to look at ac that wasn’t cooling. Found no ac connected to that room. Traced back duct work that was close by by there was nothing that suggested that room has ever had an ac in it. I explained this to manager and suggested that we could put a quote in to install a small portable unit. Manager said to hold off and they would speak to their facility manager to see what they wanted to do. Job completed | Nuisance Calls | Nuisance Calls | 0.99785
8/12/2023 9:57:08 PM Stark, Keith -0001 Found condenser fuse on disconnect bad. I replaced fuse with another 60amp fuse I found in the condenser. I checked amps L1 is 27amps L2 is 32amps and L3 is 32amps. Cases are now cooling properly. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99391
Evaporator was ice up. After the defrost process I monitored the temp drop. When alarm cleared, I check case and temps were good. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99615
7/24/2023 10:04:34 AM Emmer, Bob -0001 7/24/2023 Bob E Survey damaged to inside safety poles in MTB2/3.poles are leaning on wall panels and concrete anchors are bent and not secure or holding. Will have to cut damaged anchors out seal holes with epoxy. Level floor with concrete epoxy and installed new bigger 5/8”x6” concrete anchors and secure anchors with epoxy. Will send in quote and do all repairs when quote is approved. Is a safety issue should be addressed asap. 8/3/2023 9:34:28 AM Claudio, Anthony -0002 8/3/23 Anthony C -Checked into service channel and with MOD upon arrival. -No work can be done due to not having assistance. -Job not completed and will return tomorrow morning with non mechanical. 8/7/2023 5:57:49 PM Emmer, Bob -0003 8/7/2023 Bob E and Glenn Sr and Robert On arrival tech check in with service channel and store manager. Had to cut off bent concrete anchors then lift inside walk in cooler safety poles and move out of way. Found a lot of concrete damage. Cleaned up all broken and cracked up concrete. Filled and leveled concrete with concrete epoxy. Set safety poles in proper position and installed new 5/8x6” concrete anchors with floor shims to make poles plumb.Also repaired top U bolts and tighten down and secures top safety pole cross member. Cleaned up all area job complete. 8/7/2023 6:08:37 PM Frietze, Robert -0006 MTB 2/3 Safety Poles Quote 8/07/2023 Robert F Help technician Bob E repair safety poles. See Bob’s notes 8/7/2023 6:27:53 PM Alexander Sr, Glenn -0005 08/07/2023-Glenn Sr. Bob and Robert Upon arrival checked in with manager and Service Channel. Proceeded to cooler with loose and broken safety poles. Assisted Bob on removing poles. Filled up broken concrete with epoxy and reinstalled safety poles. See Bobs notes | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.99397
Time in 1600 Time out 1830 Call completed Check in with manager for C03b high temp -found case ice -check set point at 13 -de-ice case -called home office had set point changed to 23 | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99727
Compressor L/O alarm(s) cleared and are back online. We were on-site for the Heat Reclaim change-out and had to close off some valves to isolate the water tanks, which caused the compressors to trippin on oil L/O No issues. Call complete | Capital Replacement | Capital Replacement | 0.98261
Aug 11, 2023 Found compressor 3 tripped on oil. Found unit working correctly and found no issue. Net oil pressure is good and compressor cycled several times. If problem persists might need to replace compressor oil control. | Compressors/Motors | Compressors/Motors | 0.99866
Checked in with manger located RTU walking Checked all pressures and defrost times Employee called it in as emergency when it was on defrost Everything is good. Job completed | Nuisance Calls | Nuisance Calls | 0.99808
7/19/2023 1:50:55 PM Franco, Ryan -0001 On site. Labor: 1300-1600 Checked EP2 for potential issues. Walked the roof to see which units were not producing condensation or not running. RTU #83 only had two circuits running. CK3&4 tripped on high head pressure. No issues with condenser fan start components. Condenser motors amp draws were all within normal range. High head pressure potentially a problem during extreme ambients. RTU #12: All condenser relays not receiving 24V. Found a loose common connection. Tested. All circuits running. AHU1 Munters unit lost power to T5 XFmer. Diagnosed a dirty smoke alarm. Cleaned out and all controls turned on. All circuits operating normally. Overall store temp was at 72°f. Adjusted front and south side store temp to 70°f. It is currently 110°f. Coil cleaning for all outdoor coils is recommended in the future to help with capacity loss during high ambients. This will help with low temperature splits. All RTUs and AHU are operating normally. Job complete. 7/21/2023 6:26:43 PM Franco, Ryan -0002 Labor: 1600-1630 Travel from: 1630-1700 Checked in with MOD -David. Call was sent in unsatisfactory by mistake. Job complete. | Nuisance Calls | Capital Replacement | 0.52971
8/10/2023 Gonzalez, Steven -0001 Gp#230808-0373 Checked in with manager Lucas Working on ice cream door with broken glass Case Model#ARMZC30 Serial#0508-102674INA Contacted Anthony doors and got glass door ordered Ordered door under Sam’s account using po#253260654 No ETA available at this time Order reference#01038981 Contact information 18007720900 follow up required 9/11/2023 7:48:17 AM Gonzalez, Steven -0003 Gp#230808-0373 Checked in with manager amber Working on broken glass door replacement Located new door and uncredited Removed old and installed new door Adjusted door and installed all trim and other brackets Also adjusted door Door closing properly No other issues at this time job completed | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99724
ST/TT0530-0545 ST0545-1015 Arrived on site checked in with manager & service channel Found Dairy RCU3 at 55 Asked for roof access found RCU3offline Found breaker tripped Look for any shorts on Checked Compressor if ground it’s not grounded Checked windings okay Found contactor for Compressor pivoted Went To supply to pick up needed contactor R&R Contactor Restarted RCU Monitored opps Dropped to set point Call complete | Compressors/Motors | Compressors/Motors | 0.99853
Arrived on site and checked in with manager Luis. Had to wait to log in on service channel was on site at 0600. Looked over freezer door with issues and was not closing causing high temping freezer. Door is not able to close due to damage read over notes of last tech out for work order. POS Freezer 2 Asset Tag: 0052045 Brand: Regent KPS SN: DO.10046.2 Work was completed by general construction team on WO 230814-0233 TN 253683421. Pictures of completed work is on work order. Also went through the damage done to the POS cooler door WO 230804-0254 called dispatch and had call sent over to general construction while they are on site. Updated manager that POS freezers door has been repaired call is complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99659
8/11/2023 5:29:11 PM Decarlo, Anthony -0001 Duplicate work order, same prep table as w/o 230807-0348 | Nuisance Calls | Case Cleaning/Deicing | 0.77933
Complete assisted Greg Moran installing pull seal door safety straps. Accidentally got managers signature on the wrong ticket. Added screen shot in attachments | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99723
Replaced the contactor for compressor 4 | Compressors/Motors | Compressors/Motors | 0.99825
8/20/2023 5:13:53 PM Becissa, Bachir -0001 Called out for rack B down. Upon arrival found rack SB down. Compressor #3 had tripped breaker. Compressor megged ok, reset and checked ops. Everything checked out good. Compressor #2 kept tripping on OFC. (it’s a rebuilt compressor). Swapped out legs (L1&L2) to change the oil pump rotation. Compressor stays on running and NOP @28#. | Compressors/Motors | Compressors/Motors | 0.99854
8/17/2023 7:20:32 PM Homan, Timothy -0001 Found both LTA1 coils starting/ are iced up. Found heater switch in “ON” position but no power. Knowing that I’ve ran into other Walmart/Sams stores wired backwards, I switch them to OFF and the power restored to the heaters. Ran it through three defrosts. Will send someone back tomorrow to see whether then need manual defrosting (probably a little at least) or if they can catch up. Temps are good in box when systems are on. Not complete 8/21/2023 6:39:00 PM Soto, David -0002 -While on site inspected coils and verified all clear -defrost ops working and coils de-iced on their own -job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99853
Drove to United and picked up new module. Arrived at the store, logged into Service Channel and spoke with the manager, Alfred. I removed the existing bi metal overload. That was fried. Re did the wiring, added new wires, installed the new hybrid module. Compressor is working properly now. This is complete no need for follow up. | Compressors/Motors | Compressors/Motors | 0.98856
8/1/2023 6:28:14 AM Davila Garcia, Pedro -0001 Replaced the contactor for compressor 4 | Compressors/Motors | Compressors/Motors | 0.99841
I came and checked in with the store manager and I checked the A3 and A4 system and found that the FF2-13 door is damaged, so I sent the information to be quoted and change the new one, the A6a showcases were also checked and the A6b and I found that the door gaskets are damaged, so I also sent the information so that they can order them and come and change them. | Damage by Customer | Damage by Customer | 0.80023
8/8/2023 5:00:10 PM Stuart, Christopher -0001 En Route: 1530 Time In: 1630 Time Out: 1845 Cafe Grab-n-Go Beverage Cooler High Temping Checked into Service Channel Checked in w/MOD Johnny HillPhoenix (Cafe Grab-n-Go Cooler) M# O3 5UMA4 S# 1272545 R-404a Issues found: Dirty/clogged condenser Clogged drain screen, and water sitting in the drain pan Dirty evap. coil Flashing sight glass Discharge air temp @ 57 Work done: Cleaned condenser and evap. coils. Cleaned drain screen and cleared drain line. Leak checked case and found a small leak on the suction service port inside the case. Leak repaired. Added in 3# of R-404a into the system (truck stock). Sight glass now solid column. Case temp now @ 32 Checked out w/MOD Johnny Checked out of Service Channel Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99847
ST:17:30-18:00 OT TT: 18:00- Arrived checked in with MOD, found that the walk in cooler drain line was clogged no water dripping at this time, checked out with MOD. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99828
Sam’s club 6235 Travel start 07:00 Time in 10:00 Time out 17:15 Compressor hangs out Picked up parts from local parts house. Arrived at store and checked in with manager. Had employee remove compressor from back of truck and bring over to motor room. Disconnected all power and safety’s from compressor. Removed suction and discharge lines from compressor. Disconnected compressor from bench. Removed and installed new compressor on bench. Wired in compressor. Installed new safety’s and wired them in. Connected suction and discharge lines. Ran vacuum on compressor. Opened up liquid line and suction line and oil line on compressor. Added 2 gallons of oil to compressor and rack. Removed and replaced contactor and auxiliary. Turned power on to compressor. Compressor is running properly. Leak checked compressor and found no leaks. Job complete | Compressors/Motors | Compressors/Motors | 0.99839
8/1/2023 3:47:32 PM Maldonado, Chris -0001 Start time-1445 End time-1745 complete check in with manager Whitney checked freezer for iced up coils (no iced up coils) got roof access from manager checked roof unit for cafe freezer going off on high pressure took unit top off to get better access to Condenser coils cleaned condenser coils reset high pressure switch pressure sitting at 250 psi put top back on unit waited for freezer to get at temp checked out with manager Santiago Gonzaga | Case Cleaning/Deicing | Misc. Billable Repairs and Service Calls | 0.98235
10-4-2023 Adrian De La Cruz Jr GP# -230815-0298 PO# -253785111 1000 -1030 TT 1030 -1200 on-site Checked in with store manger in the morning. Came to replace LED drivers with my fellow tech on the POS coolers. I was his spotter We verified proper operation. -Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99586
Checked in with manager located cafe freezer operating. Freezer is at -5 must of been a duplicate Wo I worked on this freezer 2 days ago under another Wo. | Nuisance Calls | Nuisance Calls | 0.99801
7/28/2023 9:45:36 AM Fenton, Typhan -0001 Just seen This on my board not sure why 8/3/2023 6:46:53 PM Fenton, Typhan -0002 Make: KYSOR/Warren Model: TD340-092-VC-4-FHSLX-B Serial: 1112000168 Unit: Rack B & BS -upon arrival the rack was at suction set point. B was at 35 and BS was at 44. -the rack was running at suction set point and the cases were all at temp. I then checked the entire system to see what could have caused the alarm. -this was cases from the rack being down. Not sure what caused to rack to go down but I checked the condenser, compressors and refrigeration and everything checked normal. -this system was also monitored for abnormal activity but nothing was found. No other issues system operational. | Nuisance Calls | Nuisance Calls | 0.99386
Job incomplete Arrived on site for an alarm in the dairy cooler blew out the evaporator coil’s. Check the liquid levels on rack a hooked up my gauges to the filter dryer. Found a five psi difference. Need to have rack a filter dryer pull down and dryer’s. Replaced | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.79375
1030-1300 2.5 hours reg time Arrived on site, checked in with Christy, found that bakery door handles booth broken along with door seal that holds heat tape in place, ordered parts will return to install | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99601
8/2/2023 8:15:47 AM Hendricks, William -0003 Service channel would not allow me to login. I am in the process of having to correct this. I checked in with the manager about this call because of the lack of service channel access. The prep table had been shut off on my arrival with the thermostat disconnected. I reconnected the thermostat turned the unit back on. It began to run. I opened the panels and carefully inspected the electrical connections. I noticed that the condenser coil was extremely dirty so carefully blew it out with nitrogen. I then attached my gauges to the service ports and observed the refrigerant levels and pressures. After careful observation the unit appeared to be functioning normally and have the proper charge. By cleaning the coil I lowered the pressure on the unit. I returned the next morning and checked on the unit once more using gauges and thermostats. The unit is running normally now. | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.99821
7/24/2023 9:00:31 PM Paruleski, John -0001 Called out for cafe cooler warm Met with manager Inspected and found unit not pulling down to suction pressure. Gauged up to unit on rooftop and found unit cycling off on thermal overload, compressor pulling down to 85psi and then building pressure back up to 95psi (suction), head pressure sitting at 300psi. Not going off on high head pressure, compressor has failed will not reach suction. Quote to RR compressor 8/28/2023 5:05:24 PM Devlin, Joseph -0003 Assisted Rodrigo with compressor replacement. 8/29/2023 6:25:08 AM Hernandez, Rodrigo -0002 Arrived to site checked in with mod tony to replace compressor on Cafe WIC Recieved access to rooftop Recovered refrigerant charge and removed old compressor Installed new compressor and re piped lines do to lines not meeting the same as old compressor Compressor brazed in, new drier installed, new contactor and new start components Pulled 30 min vaccum Down to 500 microns and holding Opened up valves to break vaccum Added 3lbs of R404A to clear sight glass Checked all ops Compressor LPS and HPS tested and verified they are opening as set to Refrigerant flavor: R404A Pressures: Hi 300lbs low 50lbs Removed all equipment off roof and closed up unit Cooler down to sp temp of 38F and holding Verified all fans are running Cooler at temp, no alarms Checked out with mod tony Job complete | Compressors/Motors | Compressors/Motors | 0.99846
Onsite: 1500-1700 -Was already onsite on another call manager wanted me to look at produce walk in. -Produce walk in had ice starting to build up on evaporator C9b -MOD wanted me to remove ice build up before it got worse and leaks -Removed all ice on coil using hot water -made sure no other evaporators in walk in didn’t have ice build up. -made sure drains on walk in were clear as well -all ice build up removed -made sure all fans were running properly -call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99862
Job completed Was currently on site for another job spoke with the manager and she told me that they were having issues opening and closing this door to the freezer and I adjusted several places on the door to close up the gap. Got gas closed up. Everything is good at this time . | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.58805
Complete. Went to cafe, freezer asset tag did not match. Asset tag on ticket matches walk in cooler. Removed all old air curtains Replaced with new air curtains in both coolers. Checked out with manager Mhisani ford | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.84898
8/2/2023 6:50:31 PM Zaun, Paul -0001 8-2-23 Paul Z / MTA 4 drain pan is iced at drain checked in with Andy found WIC MTA has two iced drain pans sizer lift is not working will have to speak with Jeremy in the morning about possibly renting a sizer lift. cooler is at temperature with no alarms Incomplete 8/10/2023 1:32:38 PM Zaun, Paul -0002 8-9-23 Paul Z / deice drain pans / coils System MTB WIC assisted Jose C -please see notes Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99836
En Route: 0730 Time In: 0900 Time Out: 1200 CPU Freezer Running Warm (Home Office Call) Checked into Service Channel Checked in w/MOD Katrina Kysor Warren (CPU Freezer) M# FX5SL-03RUN S# C17H00393 R-404a Located CPU freezer. Case controller displaying an ER 7 alarm and case temp at 59. Removed deck pans and the fans were not running. Slight ice build up on distribution, suction line and in the middle of the coil. Put unit into manual defrost and de-iced coil with hot water. Put case back together and terminated defrost. Case temp got down to -2 after about an hour. Set point is -6. CPU freezer is right next to two exit doors, and constant opening and closing the doors let’s large amount of warm air into the case and ices up the coil. Adjusted defrost parameters for the freezer. Defrost will Now occur once every 12 hours, for 45 minutes per. Increased drip time to 3 minutes defrost term temp to 50. Checked out w/MOD Katrina Checked out of Service Channel Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99866
8/8/2023 2:53:38 AM Cosgrove, Reese -0001 On-site 1230-1315 Arrived on site. Checked in with manager, Jacob Made way to rackB. Checked comp5 on rackB Compressor was not in lockout on arrival Monitored compressor temporarily Checked gas and oil pressure on compressor All checks okay call is from July 17, possible duplicate Job complete | Nuisance Calls | Compressors/Motors | 0.99865
8/5/2023 10:48:42 PM Garreans, David -0001 TTOT 2130-2230 Time in 2230 Time out 2330 Rack A M# RNSX-D8-L064-M045-V4XLA-A S# S16H00036 Tg# 0050160 Checked in with manager Damien. Curcuits A10, A13 and A14 cases were all empty and liquid line hand valved off. Turned back on and all curcuits dropped back down to temperature. Manager on duty Damien has no clue why they were hand valved off. There was no ice and cases had good airflow. Checked out with manager Damien. Complete | Nuisance Calls | Damage by Customer | 0.58448
7/21/2023 11:14:56 AM Dankenbring, Jarod -0001 Found compressor overheating due to dirty condenser and filters. Cleaned condenser, picked up and replaced filters and all checks ok. | Compressors/Motors | Compressors/Motors | 0.99408
Jul 20, 2023 Checked case found solenoid open. System was in defrost, took out of defrost and found compressor would not run. I found and repaired a broken control wire for the contactor. System is now operational and returning to temp. | Nuisance Calls | Nuisance Calls | 0.99816
8/15/2023 8:40:37 PM Arriaga, Luis -0001 Arrived on site checked in went to rack house and found the rack down I tested for power and had power to the rack I went checked pressures rack was good hit the reset button on the head pressure and no luck I reset the boards and rack came back online I noticed the head pressure would rise real quick checked the condenser fan motors and they were running backwards I turned off the vfd and check for programming errors all working properly the rack had gone out on head pressure due to fans rotation waited till cases came down to temp and no alarms present checked out | Compressors/Motors | Compressors/Motors | 0.99804
Checked in with manager Giovanni. All employees were about to leave when I arrived. I was able to check a few things before they left. Verified no iced coils. Verified fans are running. Went to rooftop to verify condenser is running. Receiver level is 35%. Manager mentioned to me that there is a compressor being ordered and that a tech told him that it can affect the temps a little bit. Verified only 3 comps are running. Coils are at 37 degrees. -C01 & C02. Checked the other coils as well. Checked out with manager Giovanni. | Compressors/Motors | Nuisance Calls | 0.98079
On site had to locate crate finally we found it they had it hidden behind some other pallets waited for them to take out all the pallets located door that needed replacing and replaced it took old door outside along with the pallet it came in cleaned up area and checked out with Dan | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98587
7/19/2023 1:55:20 AM Toomer, Collin -0001 OT TT:18:30-20:30 OT:20:30-00:00 OT:00:00-2:00 OT TT:2:00-4:00 Arrived checked in with MOD, made way to Rack B and found rack completely down, found compressors in lock out due to high head pressure, made way to condensers and noticed that they were covered in dirt and debris, cleaned condensers for all three racks, reset rack b and still no condenser fans coming on, called Jose he advised to bypass the VFD on controller so I did and put to 60k htz. So that they would stay on this call will need Jim to follow up please since I’m not that diverse on glycol racks yet. Call needs follow up by Jim. 8/8/2023 1:00:17 PM Toomer, Collin -0002 ST:13:00-14:30 MTB -Arrived checked in with manager. -Gained access to motor room -Found MTB Discharge 264.0, suction pressure 34.5 -Receiver level 20.6% -Took full trash out and replaced the bag. -Checked all CFMs all operational -VFD is in bypass to help with high head pressure. -Checked all safety’s on compressors no issues all safety’s working properly at this time. | Compressors/Motors | Compressors/Motors | 0.99825
8/8/2023 6:26:52 PM Young, Robert -0001 Incomplete Arrived on site and checked in with the manager. Went to the roof and found the RTU 16 was idle mode. Found the main controller in the electrical room was in com loss. Rebooted the controller and the RTU’s are still com loss. Started going through the units to locate the board that is dragging the network down. Will need a com loop diagram for the communication system. Will return to finish diagnosis. 8/16/2023 6:48:56 PM Young, Robert -0002 Incomplete Arrived on site and checked in with the manager. Went to the roof and found the unit was off. Unit not showing up on the controller. Had to set the unit to run in stand alone mode at the controller. Assisted the other tech with other calls while onsite. 8/18/2023 1:17:48 PM Young, Robert -0003 Arrived on site and checked in with the manager. Went to the RTU’s and was able to get most of the RTU’s back on the comm loop. Will need to order 5 bacnet boards and 1 prodigy board. AHU1 is back online. Located a short in the unit and repaired it and the dehumidifier is back online. 9/19/2023 3:48:03 PM Young, Robert -0004 Incomplete/have to order parts Arrived on site and checked in with the manager. Went to the roof and installed bacnet boards on RTU 8, 13,14,16 and 20. Went back down to the electrical room and found the network went down again. Had to go back to the roof and disconnect the network cables from each unit . Connected them one by one and found when 14,16 or 20 is connected it brings down the network. RTU prodigy board is back on line and running. RTU 13 control transformer has failed and the condenser fan motor relay has failed. Will order parts from Lennox. 10/11/2023 2:56:04 PM Fanini, Emmanuel -0006 Work with Robert repair RTU 10/12/2023 10:41:08 AM Young, Robert -0005 Arrived on site and checked in with the manager. Went to RTU 14 and replaced the transformer , condenser fan relay and the touch screen. Turned the unit on and addressed the the board. Novar is reading the temperature, went to RTU 13 and replaced the board and the touch screen , addressed the board and it reading on novar. RTU 26 replaced the fuse and it is back online as well. All RTU’s and AHU’s are back on line. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99575
07/18/23ZP SAMS CLUB 4704 System A4 & A5 -Upon arrival check in with service channel. -Located the mod to check in. -Got access to the WIF. -Found the doors open as they are loading the box. -System had then went into a defrost on arrival -Waited for system to finish its defrost cycle. -System kicked on and waited for temps to drop. -Temps had dropped to 8F and then spiked up. -Went to the WIF found the reach in doors open as they are stocking product. -Graphed temps on the WIF, WIF drops below 2F when the doors are remaining closed. -System is operating normally. -Called home office and waited 20 minutes to get ahold of them. -Had them look at the programming for the WIF and had them change the refrigerant type from 448 to 404. -High temps are Due to heavy foot traffic and doors being left open while stocking. -Informed the mod of the situation -This call is now complete | Nuisance Calls | Nuisance Calls | 0.99837
8/18/2023 Ruiz-Serafin, Alex -0001 Rack B low receiver level-while onsite I checked receiver level it’s at 30% I torch receiver to make sure gage was working did not find any issue I informed MOD of job performed and checked out | Nuisance Calls | Nuisance Calls | 0.99812
7/22/2023 4:39:53 PM Martin Jr, Robert -0001 Found compressor 3 tripped on high head pressure. Rack discharge got up to 345psi today and pressure control was set at 300. Raised pressure control to 375psi. Found 1 fan motor now spinning. Started trouble shooting and found the contractor bad. Replaced contractor with one that was on site already. All motors are now currently running and head pressure is down to 295psi. Condensers on both racks are in rough shape, I recommend changing out condensers on both Rack A and B. Rack is currently back up and running. | Compressors/Motors | Compressors/Motors | 0.99816
Anthony Robak Checked in with MOD Whitney Went to rack b for automated call all circuits high temping Circuits were high temping while rack b was shut down on to ticket 230804-0441 Checked all temps All circuits at temp Found compressor B3 off on oil pressure Checked contactor and oil safety switch All check out but found oil control running low Adjusted oil control until it maintained oil level All comps on B side running Rack suction at temp All circuits at temp Checked out with Whitney complete | Compressors/Motors | Compressors/Motors | 0.99824
7/18/2023 11:59:03 PM SCHUPBACH, DUSTIN -0001 Took freezer door off POS freezer. Installed new heaters and gaskets installed door. We are missing a leg of power also and will need to come back and further diagnose. door is now back onto freezer. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9973
8/4/2023 1:11:48 PM Cox, Brandon -0001 Checked in with Manager Peter. Found RTU 14 mangers office felt ambient. Went to roof top to diagnose unit. Found blower door wide open. Blower was just pushing in outside air to the room. Closed door waited to check temps. Called Walmart support Found unit at setpoint. Call complete. No critical alarms. | Nuisance Calls | Non-Mechanical Door Repairs | 0.98329
Fan is leaking in the cooler / Please provide the case label number: 0129990 REFRIGERATION (FROZEN, COOLERS, DAIRY ETC.) / Refrigeration / Walk In -Cooler / Water Leak / Name: POOJA SALOOJA -p0s03pa.s04816 / Phone Number: 321-960-3738 / Tag ID: MTB-4-Cooler-POS-4816 / Brand: KPS / Model Number: Cooler-POS / Serial Number: 21672 011 / Tag ID: 0051971 / Scheduled date: July 14, 20233:24 PM 7/14/2023 10:37:48 AM Cervantes-Gonzalez, Luis -0001 Got to the location and checked in with Manager POOJA SALOOJA when up to the pos cooler and found coil # 2 with an ice up drain pan. Got with Alan and he will fallow up on this call. He will be tomorrow to de-ice it. Talked to the manger to have those two plates move from the top to give him some room. 7/17/2023 11:03:22 AM Gonzalez, Alan -0002 Checked in with Corey. Let him know I will be deicing the drain pan in the POS cooler for unit #2. Got my tools and trash can with sump pump out of my van. Set up the hoses and sump pump. Went to get hot water in the trash can. Could not get a scissor lift in there so I got a ladder and went to check out what was going on. I melted off the ice right where the drain hole was so all the water will go away faster. Noticed that the water was not going away so I checked the drain hole to see if it was plugged. There was nothing blocking the hole so I took apart the pipe for the drain. Once the pipe was out I saw there was a lot of slime/dirt so I cleaned it all out. Put the pipe back on and continued to deice the pan. After all of the ice was gone I also cleaned the evaporator coils with nitrogen and sprayed it with water as well. Cleaned up the area and put everything away. Checked out with Corey. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99839
7/19/23 Ray Gary Arrived onsite and checked in with the manager (Paul)I walked every case that was supposedly alarming I found all the temperature were fine So I checked air flow and that was good I advised Paul that I found no problems I took pictures of each case tag and temp readings and uploaded them on mobile tech THIS JOB IS COMPLETED | Nuisance Calls | Nuisance Calls | 0.99824
8/1/2023 12:58:21 PM Paruleski, John -0001 Called out for pharmacy AC too cold Met with manager Kim on arrival Inspected and found pharmacy cold at 68 Inspected unit and found unit running. Contacted Walmart home office and had temp setpoint changed from 71 to 73. Home office was reading a temp of 70 in the pharmacy, but could only bump up the temp 2 degrees. Monitored and verified temps increased slightly. All ops check good | Nuisance Calls | Nuisance Calls | 0.99828
MOD Ed -checked in with Ed and he informed me not to look at the snack bar freezer that the alarm was cas used by the door being left open too long -Ed directed me to the middle freezer and instructed me to focus on that -found that the door had been hit with a for lift and knocked off the track -the front end wheels were not on the track at all -sourced equipment form truck and retuned to get door on track -had to use prybar to slide it to the end were I could reposition the wheels and get it back on the track -once on the track I opened and closed it a few times -Cody MOD came and verfied it was working -found that it is missing the stoppers to keep the door from coming off track -Manufature is closed, will pass this on to CFS to get parts ordered to get the door its stoppers Checked out with Cody and let him know the WO will be in parts on order for now until we can source the parts. PARTS NEEDED Please Order two door stops please PN listed below. SYS Freezer #2 (middle) Asset Tag: 0052045 Brand: Regent KPS Model: n/a SN: DO.10046.2 Manufacture #: 800-826-3100 PN: 23-000822 Link: https://parts.kpsglobal.com/PublicStore/product/DOOR-OPEN-SIDE-STOP,284,153.aspx C.O. DIS: Breanna Placed in parts needed. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9546
8/15/2023 5:40:45 PM Rudnick, Bryan -0001 Arrived at location, checked in with manager Erik. Let him know I am here for leak detector box broken in pos cooler and is alarming. Manager Erik told me one of his associates bumped into leak detector box, that may have tripped it. Proceeded to check leak detector box to verify its not broken. Leak detector light is going off. Brought leak detector in and leak checked the store and pos cooler. No leaks detected in store. Went leak detector control box and cycled power to reset leak detector box. After I reset leak detector box. All leak detectors are in OK status and are running at normal operations. No alarms present. Cooler is at set point temperature and all cases are temping properly. Let manager Erik know the resolution and leak detector box is good to go and no leaks. POS Cooler Zone 3 leak detector box Brand: Emerson Model: MRLDS-250 Serial: 20082085 Checked out with manager Erik Call complete | Damage by Customer | Nuisance Calls | 0.97145
10-5-23 Paul Z / LTA4B Grocery freezer LTA4B checked in with Jeremy checked WIF LTA found box at 5F checked controller temperature found box was in defrost LTA 5a&5B and LTA 4 A&B are high temperature after defrost circuit timed out monitored temperature LTA 4B & 4A came down in temperature to -2F distribution tubes, orfice and temp sensor was changed checked coil for ice build up -there is no ice on evaporator Job completed | Nuisance Calls | Nuisance Calls | 0.99821
7/31/2023 7:32:07 PM Garreans, David -0001 Checked temperature and case was at setpoint temperature. Manager Payne told me to close ticket. Complete | Nuisance Calls | Nuisance Calls | 0.9978
8/18/2023 11:25:56 AM Nichols, Cooper -0001 Arrived for suction # alarm Rack BS Rack running @ 52# on arrival with no alarm present Adjusted sub cooler EPR and Txv’s Now subcooling solenoids are shutting down subcooling is achieving temp. When subcooler solenoids shut down rack BS suction # drops to now low 40’s from 52#. No alarms @ departure | Compressors/Motors | Compressors/Motors | 0.89268
7/20/2023 9:11:34 PM Munoz, Julio -0001 Sams club 4822 Wo#230720-0344 Po#251410835 Rack A -upon arrival to the store and I introduced myself with manager -call home office and asked at time it was created this call and they mentioned at 14:30pm and this call was dispatch at 19:00pm -over the phone we confirmed Rack A it is operating good with no alarms, having a 15psi suction and 225psi on discharge -job completed | Nuisance Calls | Nuisance Calls | 0.99794
I arrived at the store and checked in on SC. I spoke with the MOD and he informed me that the call was completed by another company. Call complete. | Nuisance Calls | Nuisance Calls | 0.99829
8/1/23 TH TT: 8:00-8:45 Time in: 8:45 Time out: 11:00 LTA-2: Rollseal Door MN: RS-500 Track Kit SN: 0009113 Checked in with Service channel and MOD (James). Checked the location and found Rollseal doors cannot moved because the blanket was tangled. Turned off the power. Unlocked the breake of Motor and managed the Rollers and Blanket. Locked the Breake of lift motor. Turned on the power and set programmed to the Manual mode. Checked Door operation. It’s can open and close now. This Door needed to be replace and New Door is already order. Just waiting shipping to the store and replace in another work order (Refer WO# 230625-0059). Cleaned work area. Informed and checked out with MOD (Josh) and Service channel Job finished | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99665
Job completed. Spoke with manager and informed her why I was on site. She informed me what was needed. There was two lights damaged in the wall-in freezer (LTA-3). One light had just seemed to be twisted at the conduit. The other like had a broken light diffuser. Will need to refer this to an electrician who can gather the parts and do repairs. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99389
Was already on site, found faults alarm on compressor 6 rack. Core sense had 2 flash alarm, lock rotor amps Check for voltage at contactor found contactor pitted not allowing all 3 legs to power compressor. Remove failed contactor with auxiliary. Installed new contactor with auxiliary. Check amps on compressor once parts were installed. Check wiring ensure connections are secure. Alarm is clear on compressor. All at normal at this time Parts used Auxiliary contactor call is completed. | Compressors/Motors | Compressors/Motors | 0.99849
TT 1030-1430 Time in 1430 Time out 1700 Call complete Arrived check in with manager for server room and manager office hot -found RTU running high pressure due to extreme heat and dirty condenser -went to Home Depot picked 400 feet of water hose -ran hoses across the roof and cleaned condensers -drop head pressure -called home office they said RTU are in comm loss -reset controller got communication restored -left hoses on site | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99731
OT TT:16:00-16:45 OT:16:45-17:30 Arrived checked in with Kaye Located freezer in curb pick up, MODEL: FX5SL -O3RUN SERIAL NUMBER: C17H00393 Upon arrival freezer at -4 degrees Checked condenser it’s clean, spoke with curb side manager she said that the manager that sent in the call said it wasn’t at temp and said def on screen. Unit was in defrost when she seen temp and called this in no issue found freezer is working Spoke with manger Kaye about it. Checked out with manager Job complete. | Nuisance Calls | Misc. Billable Repairs and Service Calls | 0.60906
Was already on site and went over to case CS12A, where you can hear the fans tapping water. -I first removed the product from the bottom shelving to access the coil -found the condensate drain line plugged -went to the floor sink, removed paneling, removed debris clogging the floor sink -blew the clogged drain line out with C02 -once all water was drained, I cleaned up all slime and debris from the case, rinsed out with water, and removed debris from the floor drain -placed all parts back together, checked all ops, and the case is now cleaned and properly draining -this call is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99844
ALREADY BILLED, CANNOT TRANSFER 9/14 DUPLICATE TO to 230814-0233 / TRANSFER COSTS 8/3/2023 9:44:32 AM Villeda, Luis -0002 Checked in Jeremy about a follow up on Freezer Door, Door is missing door stop and a it looks like a sensor, we let Jeremy know that parts will have to be ordered , will order parts with Lawrence, we told Jeremy we would give him ETA on parts once we get that from Lawrence. Call Incomplete. 8/3/2023 12:26:57 PM Rodriguez, Johnson -0001 door checked and found off track put back on track door parts need to be ordered. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99526
7/31 Time in 09:15 Time out 10:45 TT to united 11:30 Used scissor lift to access evaporator in meat market. Will need to return with new motor and deice coils. Floor drains are clogged right now in meat department. Do not want to deice coils and flood back area. 08/2 TT 11:00 Lunch 12:00-12:30 Time in 12:30 Time out 19:00 TT 19:30 Checked in with manager. Was told I need a certain tool for packing nut leak. Went to united to get one. Waited for the scissor lift to be finished with when they were working on sprinklers. Washed both coils. Changed fan motor and blade. Adjusted superheat. Cleaned up. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99784
found rack off on high head and tripped vfd. repaired short and reset vfd, fans are on. comp 2 has a new current sensing relay ordered | Compressors/Motors | Compressors/Motors | 0.99822
7/27/2023 3:29:50 PM Haddad, Masoud -0001 Arrived on site checked in with the manager -found the walk in cooler in the cafe on high temperature -walk in cooler MT-1 -found the condenser on the roof is down -after troubleshooting found the high pressure switch is tripped -found the condenser coil dirty -cleaned the condenser coil and reset the pressure switch and the unit start running and start cooling -waited till reached 37 degrees -condenser fan running normally -checked pressure and no restriction found and the pressure is normal -all checked good -calm completed | Case Cleaning/Deicing | Misc. Billable Repairs and Service Calls | 0.61842
OT TT:18:45-19:45 OT:19:45-21:30 OT TT:21:30-23:30 Arrived checked in with MOD, gained roof access pharmacy was closed, found RTU 16 and checked pressures and system operations, called home office to check sensors and they said ODT is reading 67degrees and that the system was in com loss, spoke with Keith and was advised that there was a sweep done on this roof and that the company that did the install hasn’t finished the job. So no com wires are ran to that system the other company will need to finish. System is working like it’s supposed to and the unoccupied set point is set the 73degrees and system was satisfied. I couldn’t check the temperature inside pharmacy due to them being closed. Checked out with manager job complete. | Nuisance Calls | Nuisance Calls | 0.99813
7/28/2023 1:53:25 PM Moran, Greg -0001 Completed arrived met with manager. Repaired 5 different pipe insulation tubes. | Misc. Billable Repairs and Service Calls | Damage by Customer | 0.7533
Found compressor shorted to ground. Have new compressor on order. Will return to install once in. | Compressors/Motors | Compressors/Motors | 0.99858
8/14/2023 6:11:26 PM Hanamornsate, Thirathanawat -0001 8/14/23 TH Time in: 16:00 Time out: 19:15 LT-CU2: Cafe FZR Heatcraft MN: LET065BEK SN: T12A15382 Arrived on site and checked in with Service channel and MOD(John). Found Evap Coil iced up and box running 28 Degrees F because the strip curtains were opened and slide to both sides. Turned off the Breaker. Ran the water hoses. Take all Fan guards and Fan blades out. De iced the Coil. Put Fan blades and Fan guards back. Found drain pipe (PVC section) was broken. Went to Home Depot for pickup parts. Went back to the store. Removed bad Drain pipe out and installed new Drain pipe in place. Water test and no leak. Turned the breaker on. Called defrost and heater are working good. Called refrigeration mode and checked the temperature showed 11 degrees F. Needed to be close the Door longer but the Employees needed to be open for pickup product inside. Cleaned work area. Informed and checked out with MOD(Lakisa) and Service channel. Job finished | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
Time in 1130 Time out 1400 Arrived on site checked in mod CHRIS and service channel. Proceeded to WIC found temp at 21 degrees too cold. Wic controlled by pressure, found preusre control set to 50 which converts to 18 degree coil. Moved up to 60 which concerts to 23 coil temp. Let system run a few cycles te.p after adjustment 38 degrees. Checked out mod CHRIS and service Chanel. JOB COMPLETE | Nuisance Calls | Nuisance Calls | 0.99807
12-4-2023 Adrian De La Cruz Jr GP# -230801-0372 PO# -252504701 1700 -1730 TT 1730 -1900 on-site Checked in with store manger Amy Rhea. Located freezer door handle that needed to be replaced because it was damaged. We took off the damaged door handle parts and replaced them with the new door handle parts that we got ordered in back home in El Paso. Me and my partner coordinated taking it apart and putting it back together properly on the freezer door. When we were done we tested the new installed freezer door handle to make sure it was opening and closing correctly. -Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99709
TTOT 1730-1830 Time in 1830 Time out 2100 Checked in with manager Andre. C01a Hussmann M# F12G S# MY18F043041 Tg# 0031735 There was about 2 feet of case that had no airflow. I valved off case and let it air defrost for a while then turned back on. It now has airflow. No temperature issues. Checked out with manager Benny. Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99587
Time in 1445 Checked in with manager Stated coil leaking in walk in cooler MTB-2 Coil MTB-1a iced up Deiced coil so it could drain properly Cleaned up residual water with a rag from bottom of coil Talked with manager and maintenance will clean up water on floor of cooler with floor machine Checked out with manager V | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
Sam club #: 6619 System: C7/C8 SC: 230716-0186 PO: 251002078 —————— 7/17/23 Kenneth St.Amant No Travel Onsite-13:00-16:30 Checked in with manager Arrived on site checked in with location gained access. Took the pee trap off and it was full with a lot of gunk in it Took Co2 to blow all the gunk out of it Took water to to make sure it flows good Put pee trap back together Put case into defrost and watch to make sure no more water was splash around in the walk in cool and no more water was splash around Drain is clear and clean Checked out with manager Hector Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99691
8/12/2023 9:18:33 AM Stark, Keith -0001 Found lta4a evaporator vibrating heavily. Both fan mounts have cracked. I’ve shut lta4a and b evaporators off. Lta5a and b are still up and running. I will return to repair the brackets or order them. 8/18/2023 1:33:54 PM Ervin, Randy -0003 Removed fan bracket on A4 coi and welded it. Install | Compressors/Motors | Compressors/Motors | 0.44603
7/27/2023 4:03:15 PM Brooks, Brandon -0001 Sn# Sam’s Club 6624 Sc# 230727-0159 Po# 251956177 System: RCU Cafe Cooler “Leak detection alarm” Upon arrival checked in with MOD and ServiceChannel -Leak detection alarm and siren going off on RTC-Cooler on Cafe -Used electronic Leak detector in cafe and cafe cooler. No leaks detected -Located leak detector module in Cafe Cooler -Leak detector module looked as though it had been hit off the wall -There was no green power light on the face of module upon arrival -Reconnected face to module and green power indicator light turned on -Verified module face was working properly by swapping with a known functioning module -Module working properly -Reset leak detection alarm in electrical room -All zones enabled -Informed MOD of work performed and obtained a signature before my departure. Job complete | Nuisance Calls | Misc. Billable Repairs and Service Calls | 0.75129
8/3/2023 7:04:45 AM Rodriguez, Johnson -0001 alarms and systems were checked and everything was found working. | Nuisance Calls | Nuisance Calls | 0.98945
Arrived on site to work on bunker case leaking water I checked in with manager to let them know what I was doing then I went to the case and pulled the bottom of the case to access the drain and I had them pull a section of the case so I can get to the drain pan once they moved it all I removed the shelves and the fan motor and saw the drain pain had been rusting out and is leaking thru little holes so I talked to the manager and ask if they wanted to shut it off for a day and let it dry out so we can seal the pan but they said the remodel gets started on the store in a month so don’t worry about the pan | Case Cleaning/Deicing | Damage by Customer | 0.98174
Have added water hoses and sprinkler to condenser to keep head pressure in range due high temperatures and coils are deteriorating all compress running | Compressors/Motors | Compressors/Motors | 0.99756
8/13/2023 11:51:58 PM Cosgrove, Reese -0001 On-site 1830-2100 Arrived on site. Checked in with manager, Kristin bc Made way to cases d4.1a/b Case 4.1b high temping due to frozen evap coil Plastic cover panel at bottom of case was hanging off and corner was stuck in the fan blade causing fan to stop running Removed panel and fan turned on and ran normally Removed back panel to access coil and used hose to deice Cycled case back on and temp dropped to 30° Both cases 4.1a/b are at 30° and operating properly Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99825
Completed Assisted tech with scissor lift & work order. clean dust per manager request | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.9853
7/24/2023 12:52:49 PM Bargas, Jose -0001 Got the call while onsite. I checked Rack b and found that compressor b1 is bad and shut off. The compressor is on another work order. I will complete this out, and the work will be done on the original work order. Im sure its being ordered on the original work order | Compressors/Motors | Compressors/Motors | 0.99842
door checked and found off track put back on track door parts need to be ordered. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98954
080523 Alfredo Cake case warm System MTA16/MTA9 Tyler Mod:N6DL12 Ser:5158261 TT/OT-1630-1730 OT-1730-1930 Arrived at location and checked in with service channel and store manager. Bakery manager not on site and employee called manager and stated cake cases warm earlier in the day. Located bakery cases and asked manager to please move a couple of sections from both cake cases to check operations. Found all fans operating for both cases and no ice build up. Found one case with standing water due to debris and gunk blocking water flow. Both cases at temp. Cleared gunk blocking drain and used water to clear remainder of gunk and now water draining properly. Checked suction pressure for both cases and both at 55psi with a discharge air of 33°. Informed employee he was able to put all product back in cases. Call completed. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99811
Rack Associated: CLTA Systems Affected: Rack / Comp%2eiOilLockoutCompVS / ALARM Alarm Message: COMPRESSOR LOCKOUT Manual Comment: Automated WO HOME OFFICE ONLY Refrigeration -HO Use Only Rack House Compressor Lockout -Single Raised By: AUTOMATED WORK ORDER Contact: AMBER HAZELTON Position: Store Manager Scheduled date: July 23, 20237:01 PM 7/25/2023 10:03:21 AM Braswell, Caleb -0001 Arrived at location checked in with manager Jim gained access to roof inspected rack A and verified that it was compressor that has been ordered for replacement system circuit switch is shut off and main power breaker shut off called monitoring and spoke with Carlos who stated he overrode compressor off so that it would not send alarms no further issues at this time. | Compressors/Motors | Compressors/Motors | 0.9986
8/2/2023 7:17:00 PM Lawson, Christopher -0001 Completed Checked in with manger on site went to roof top for grab and go case unit found it wasnt running so inspected everything found it had a bad contactor so replaced contactor with a new one everything came on as it should an started dropping temp no other issue found. 8/2/2023 10:06:28 PM Cervantes, Carlos -0002 No travel: On-site: 1400-1700 On arrival checked on with store manager. Stated that the grab and go cooler is running warm. Verified i had air flow and all evap fan motor are working properly. Went to roof top to locate remote condensing unit -3. Found condensing unit it off and and after inspection found that i had a bad contactor. Went ahead and replaced contactor with new and started up unit. Verified unit is now running and clear aight glass. Monitor case and temps are back at set points. Notified manager about findings and CALL IS COMPLETE. | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.74672
10/23/2023 4:17:08 PM Toomer, Collin -0001 ST:11:30-16:30 TT:16:30-17:30 OT TT:17:30-18:30 Arrived checked in with Donna Located rack B on the roof and noticed the receiver level around 18-19% I began leak searching the rack and the cases associated with the rack. Found leak at compressor 3 where it was valved off but the packing nut was leaking. Rack B: Mode 1 TD600 -120 -VC-4-FXSLH -B Serial Number S15A00080 R407A Went to United and picked up 50lbs of refrigerant and added to the system. When left receiver was at 35%. Checked out with Donna. | Compressors/Motors | Compressors/Motors | 0.99754
DESCRIPTION: The job was completed. Checked in with the manager Francisco. The restaurant level of the compressor #1 was very low. I saw the leaking area with the sign of oil splash on the compressor mounting place. Performed gas leak detection on evaporator coil, expansion valves, condenser coils, and compressors. There was a small leak on the high side service port, and tightened the Schrader valve core, and replaced the old caps with new ones for the service ports. Sealed the caps with thread sealant. Charged the 14 lbs of R410A from my truck stock. All the four compressors are working properly. The AC RTU 7 drains much condensation water properly. The job was completed. | Compressors/Motors | Capital Replacement | 0.52744
Brandon Cox 08/4/23 Travel 0800 Arrival 0845 Departure 1045 Checked in with Manager Peter. Found RTU 14 mangers office felt ambient. Went to roof top to diagnose unit. Found blower door wide open. Blower was just pushing in outside air to the room. Closed door waited to check temps. Called Walmart support Found unit at setpoint. Call complete. No critical alarms. | Nuisance Calls | Non-Mechanical Door Repairs | 0.96396
On-site for previous ticket On-site for Bakery freezer roll seal door not closing Had to remove poles and straighten out tarps Found safety strapped was pulled all the way down causing door to not properly open/close Adjusted strap to correct length Checked all ops and parameters Adjusted down speed lower to prevent tarp from getting stuck Found home switch flipped wrong way, adjusted switch direction Strapped down strap to prevent anyone from pulling strap down by accident to prevent any more calls for this door Checked all parameters and ops Door is now properly closing and opening with no issues Checked out with mod Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99297
8/9/2023 7:42:23 PM Alvarado, Christopher -0001 At site meat case leaking water. Removed rail in front of case then kick plates. Located drain that’s overflowing due to floor drain being clogged. Cleared floor drain case started draining poured hot water in case for about ten minutes draining properly. Placed kick plate and rail back in place. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99834
8/22/2023 1:12:36 PM Brandau, Kenneth -0001 Arrived at the store, logged into Service Channel and spoke to the manager Stacy. I looked at A 6.1, A6.2 and all the bunkers and all temperatures are down to setpoints. With good cold airflow. I spoke to Stacy and told her what I did, and what I found. This is complete no need for follow up. | Nuisance Calls | Nuisance Calls | 0.99763
7/31/2023 9:25:40 PM Toomer, Collin -0001 OT TT:18:45-19:45 OT:19:45-21:30 OT TT:21:30-23:30 Arrived checked in with MOD, gained roof access pharmacy was closed, found RTU 16 and checked pressures and system operations, called home office to check sensors and they said ODT is reading 67degrees and that the system was in com loss, spoke with Keith and was advised that there was a sweep done on this roof and that the company that did the install hasn’t finished the job. So no com wires are ran to that system the other company will need to finish. System is working like it’s supposed to and the unoccupied set point is set the 73degrees and system was satisfied. I couldn’t check the temperature inside pharmacy due to them being closed. Checked out with manager job complete. 8/2/2023 6:43:14 PM Upchurch, Keith -0002 Time in 1630 time out 1900 Arrived on-site checked in with manager and the pharmacy. Went to roof and found unit operating properly. Called monitoring and they said that all rtus are in comm loss. Then they looked in opus and found some rtus communicating and some are not. Went to roof some rtu and ahus are turned off and some have no power coming from main breaker boxes. Also found the set points for the pharmacy at 73 degrees. Monitoring set the setpoint for ac to 71 and system is running now at 71 degrees. Call complete | Nuisance Calls | Nuisance Calls | 0.99785
Sams 4718 South Jordan 7-18-23 Wo 230716-0187 Po 251002158 MTB compressor 5 L/O Job complete Travel 1015-1045 w/ pats p/u On job 1045-1300 had part on order but was able to find locally Picked up replacement Returned to store Replaced sentronic 3 OFC Replaced old pitted Contactor Replaced auxiliary switch Re-ran new L2 wire insulation melted Compressor now running Drawing around 38 amps at start Drawing about 28amps running Replaced 5amp 250 fuse in B4 switch All compressors now running | Compressors/Motors | Compressors/Motors | 0.99866
Motor has been order at Granger Laffayette will be 9 /22/23 | Compressors/Motors | Compressors/Motors | 0.87294
GP#230723-0020 0730-1130 TT 1130-1430 RT Traveled to Roswell, NM Arrived at store and checked in store manger. Checking fuel station ac unit not working. Lennox split system unit Model XC13-018 -230 -01 Serial 5806B03579 Found a dirty filter (15x20x1) and defective condenser fan motor. Drove to parts house and got all needed parts. Replaced filter, condenser fan motor, and high pressure switch. Also run capacitors. Unit properly working. Job complete. Note: no zone sensor, unit running on mechanical thermostat. | Compressors/Motors | Compressors/Motors | 0.99428
Door doesn’t roll down FRESH MEAT Please provide club managers c 7/25/2023 10:11:57 PM Villemaire, Ryan -0001 Arrived to location, checked in with manager Kyle. Found roll up door displaying fault —-which is unknown position indicated. Opened access to door found door completely separated and not sitting in proper position looks like someone manually opened and closed door. With other techs assistance, manually fixed position of door. Once door was fixed, ran through troubleshooting. Found AC drive going in wrong direction. Found AC drive is bad. Door will have to manually be opened and closed untill new ac drive arrives. Checked with it with manager Kyle. 7/27/2023 9:20:36 AM Braswell, Caleb -0003 Arrived at location checked door and found that door material was all tangled up had to manually adjust door to straighten out material after straightening out had to re adjust emergency exit strap after re adjusting system was alarming for unknown position tried to re position door but door would only close and would not open indicating that ac drive was damaged possibly due to a power surge at store manufacture was closed as this was diagnosed will be calling in the morning to have new ac drive NDA if in stock will update work order after I contact manufacturer 7/29/2023 12:40:19 PM Braswell, Caleb -0005 Returned to location installed new AC motor drive control after installation had to reset door parameters after resetting verified operation of door no further issues | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99649
TT 0800-0900 Time in 0900 Time out 1030 Call complete Arrived log into service channel and check in with manager for LTA.5 running high temp -found product blocking air -managers were in a meeting waited for them to finish -the manager said a noise was coming from the case last night -had product pulled coil is not ice up and fans are working -manager had case properly restock | Nuisance Calls | Nuisance Calls | 0.99812
Completed. New fan motor and fan blade installed, unit is no longer making loud noises. | Compressors/Motors | Compressors/Motors | 0.99798
En Route: 1530 Time In: 1630 Time Out: 1845 Cafe Grab-n-Go Beverage Cooler High Temping Checked into Service Channel Checked in w/MOD Johnny HillPhoenix (Cafe Grab-n-Go Cooler) M# O3 5UMA4 S# 1272545 R-404a Issues found: Dirty/clogged condenser Clogged drain screen, and water sitting in the drain pan Dirty evap. coil Flashing sight glass Discharge air temp @ 57 Work done: Cleaned condenser and evap. coils. Cleaned drain screen and cleared drain line. Leak checked case and found a small leak on the suction service port inside the case. Leak repaired. Added in 3# of R-404a into the system (truck stock). Sight glass now solid column. Case temp now @ 32 Checked out w/MOD Johnny Checked out of Service Channel Job Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
Completed arrived met with manager. Replaced emergency straps on bakery freezer and cooler roll up doors. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99695
8/4/2023 11:28:11 AM Oertel, James -0001 This compressor is being replaced today on another work order . | Compressors/Motors | Compressors/Motors | 0.99856
Incomplete. Checked in with management upon arrival. Located bs04a with puddle of water underneath. Blew drain line out and poured water to check if line was backed up. Noticed case leaking from corner near frame. Will return tomorrow to reseal corners and edges and recheck. Bs05a and a10a were dry. Will pour water and try to recreate leak and resolve. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9962
Arrived on site and checked in with manager Nick. Case is low temping for LT-SC SD FF2a. Could not find case on sales floor or any where in the store. Spoke with manager and no manager or supervisor in the store knew anything about this case. Got with Novar and Walmart building controls and they had no info on location of the case. Manager said they have had this happen before and to return to speak with other manager at another time to locate case. Updated manager call in progress | Nuisance Calls | Nuisance Calls | 0.99495
7/18/2023 1:21:50 PM Elliott, Steven -0001 Reg Travel:0700-0900 Reg Labor 0900-1130 Lunch: 1130-1200 Reg Labor: 1200-1530 Reg Travel: 1530-1630 Arrived on site, checked in. Located Bakery freezer, bottom of coils frozen and drains frozen, both units are in defrost. Ran into Charles inside store he asked me to check the RTUs around the medium temp cases and redirect the discharge air from RTUs around he medium temp cases because of cases sweating. Located three RTUs 15,16 and 17 that are above the medium temp cases, checked there operation RTU 15 and 17 operating properly. RTU-16 not calling but blower has the VFD bypassed and runs all the time. Went to Bakery freezer and deuces the coil and drain. Cleared drain. 7/18/2023 3:13:24 PM Lopez, Miguel -0002 Completed Assisted tech with scissor lift | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
I arrived and checked in with the curbside manager. We removed the hinges from the old freezer door. We disconnected the heating wire from the old door. We prepared the new door for installation. We removed the old door and placed the new door on hinges so that freezer would not lose temp during installation process. We installed new top hinge. We adjusted the tensioner so that new door will now close properly without having to be manually shut every time. The door now opens and closes properly. We informed the manager that a new sticker will have to be printed for the new door. The old sticker was too old and fragile to remove intact. We checked out with the manager. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.97808
Cody warden 7/21/23 Travel – 1030 Arrival – 1115 Departure – 2000 Assisted tech on site with compressor swap. Installled TXV and Filter Dryer. | Compressors/Motors | Compressors/Motors | 0.99862
Start time-1100 End time-1300 complete checked in with manger checked rack c condenser coils and set point in rack room c18a running hi but c18 b running at temp went to check out case iced up due to fan unplugged de-ice coil and plugged fan in waiting for case to hit set point and put case back together checked out with manger | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.68579
Upon arrival located manager to start job, found that several compressors was off on oil safety reset compressors checked oil separator had two balls floating and compressor oil level 3/4 full on all compressor watch temperature drop to the negative digits all ok at this time complete | Compressors/Motors | Compressors/Motors | 0.9986
0945-1015 travel 1015-1145 Called out to restart meat case that was warm Met with manager Dahlia on arrival Inspected and found unit completely defrosted. Restarted and monitored. Waited for case to drop to temp and initiated defrost. Heaters are energized. All ops check good on departure | Nuisance Calls | Nuisance Calls | 0.99543
Got the call while onsite. I checked Rack b and found that compressor b1 is bad and shut off. The compressor is on another work order. I will complete this out, and the work will be done on the original work order. Im sure its being ordered on the original work order | Compressors/Motors | Compressors/Motors | 0.99846
Completed Checked in with manger on site went to cafe case was told water was lecking from sides so went behind case and took bottom panel off. Found drain stopped up sohad them pulled product in case to get to drain waited about 30 mins then seen sitting water in case so blow out drain with co2 3/4 times then noticed more water on floor. Went behind case and noticed floor drain wasnt draining so tryd to clean up some of the stuff in drain. Told manger gip going to need a plumber out for the floor drain but case is draining good now now other issues | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99826
8/29/2023 11:24:24 AM Jones, David -0001 Located case and it’s not in alarm it’s at set point 30 degrees. | Nuisance Calls | Nuisance Calls | 0.81512
7/31/2023 9:40:40 PM Carbon, Samuel -0001 I arrived at the store and checked in on SC. I spoke with the MOD and he informed me that the call was completed by another company. Call complete. | Nuisance Calls | Nuisance Calls | 0.99813
Arrived on site checked in with manager and service channel.located rack c . Found compressor 4 turned off . Checked all electrical and compressor. No issues wrong . Turned compressor on and rack liquid levels are at 30% . Found no signs of low liquid levels low . No alarms at this time . No further issues all cases at temp . Job complete 1600-1800 labor OT 1800-1900 travel home OT | Compressors/Motors | Compressors/Motors | 0.99635
Found a bad time delay relay on compressor number 4 . I had the part on my truck , grainier pt number 1YDD4 Truck 8037. Job complete. Rack A | Compressors/Motors | Compressors/Motors | 0.9977
7/14/23 Sam’s club 6628 Controller MTC & LTA issues. Alex Medina arrived on site , checked in on IVR and MOD Alvind. Call was for MTC rack showing as LTA and vise versa. Headed to machine room. Checked controllers on rack. MTB controller showing proper circuits and info as it should for medium temp. LTA controller showing proper circuits and info as it should for low temp. Power cycled each controller including the building controller. Contacted home office and confirmed all racks communicating. Per home office, all racks indicating proper levels and info on their end. No issues on their end. Tested each controller by putting multiple circuits through a defrost to confirmed proper ops and communicating. All ops okay. Racks at suction and maintaining. Informed MOD. CALL COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99618
Time in: 1030 Time Out: 1045 LTA 02 POS Freezer High Temp (H.O. Automated Call) Gained access to LTA Rack. LTA A02 reading -2 degrees. Not sure what caused extreme high temp. No issues found. | Nuisance Calls | Nuisance Calls | 0.93881
7/25/2023 6:32:36 PM Alexander Sr, Glenn -0002 07/25/2023-Glenn Sr. and Bob E. Tech on site. Proceeded to merchandiser freezer. Found condensate pan overflowing cause water to leak onto the floor. Found condensate pan burned out drove to parts house and picked up new condensate pan. Installed new condensate pan and cleaned evap coils with brush and coil cleaner. Job Complete 7/26/2023 4:46:55 AM Emmer, Bob -0001 7/25/2023 Bob E and Glenn Tech already on site check in with service channel. Helped Glenn replace condensation pan on top of self contained case. Also found dirty evaporator coils on case and on adjacent case brushed and clean coils and use coil cleaner on both evaporator coils are both cases. Also cleaned and dried up all water on top of the case and floor. See Glenn’s notes and pictures job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.98978
7/25/2023 10:53:44 AM Maldonado, Chris -0001 Start time-1100 End time-1300 complete checked in with manger checked rack c condenser coils and set point in rack room c18a running hi but c18 b running at temp went to check out case iced up due to fan unplugged de-ice coil and plugged fan in waiting for case to hit set point and put case back together checked out with manger | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.98756
Travel 0800 Start 0930 End 1730 Water leak in dairy cooler Checked in with MOD Got scissor lift access and store spotter Found water leaking from unit MTC1 & 2 Both units Fans running Turned off C1 dropped both coil drain pans found gunk build up in both coil pans washed and cleaned both pans found gunk frozen bottom of coil used map gas to de ice it off. Top inside of coil dirty brushed and used CO2 to clear dust off coil put unit back turned fans on. Turned off C2 Opened up unit found coil drain pans dirty cleaned and rinsed pans deiced junk off bottom of coil with Map gas inside coil dirty brushed and used CO2 put unit back fans running. Found water leaking from fire sprinkler notified MOD to get plugging out right away to fix that problem Checked out with MOD CALL COMPLETE | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99851
8/10/2023 5:22:33 PM Cho, Yoonhyun -0001 TIME: Overtime 1700 to 1730, 0.5hr Overtime travel 1730 to 1915, 1.75hr DESCRIPTION: Checked in with store manager. Checked the assignment comparing the Asset numbers, and realized that this ticket was duplicated, because another tech Jeremy commented the job today with a helper tech. So the job was completed by another tech Jeremy and his helper today. | Nuisance Calls | Nuisance Calls | 0.99833
0800-1730 9.5 reg time Acquired new compressor for rack B comp 1, took apart old compressor and removed from rack, used crane to install new compressor and wiring, pumped down compressor, opened compressor up on liquid and suction lines, checked over amp draw is average is 7amps, used leak detector and soap bubbles to check for leaks and all clear, compressor is functioning properly cleaned up work area and checked out with manager Tom | Compressors/Motors | Compressors/Motors | 0.99861
8/18/2023 9:17:36 AM Authement, Corey -0001 Checked found ice building up in drain pipe found drain insulation found bad heater need to get pipe and drain heater de ice drain pipe due to drain heater not working found lose wire on wire nut pipe ice damage pipe repaired pipe repaired insulation tested deforest ok | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.8858
B5c Hussman M# F-8G S# MY22G070125 Found no air flow at at honeycombs. Connected to case with Sporlan app, found temp at 37°, set point 22°. Alarm for incomplete defrost. Graphed temps found average climbed last 5 days. Graphed cases A and B on circuit on lcd at rack. Found they have been at set point the last 5 days. Had product pulled found both fans working, coil with frost build up. Forced defrost at case found heaters getting 0V. Removed bumper guards and dropped control panel. Traced defrost wires to breaker. Breaker with 0V, relay with 0V, and found 208v at terminal. Had to cut all zip ties and check all wires, found loose wire at terminal. Pulled fuses at rack to defrost circuits and placed wire back on terminal. Forced defrost and found heaters pull correct amps. Forced defrost and frost cleared. Case with good air flow and pulled to set point. Call completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99757
8/9/2023 11:53:02 AM Rivera, David -0001 8/9/2023. David Rivera checked inn found the fans guards that needs changing got parts number and went to united to pick up guards came back and installed new blue fan guards. Job is complete. PO#64788 | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99576
Arrived on site and checked in with manager skyla. Gained access to roof and started checking for a compressor that was locked out. Didn’t find one in rack b went to rack a and started checking over the compressors. Didn’t find one tripped. Looked over compressor 1 and it was running properly and had oil in the reservoir. Checked pressure of oil pump compared to the suction pressure and suction pressure was 18psi and oil pump pressure was 60psi. Checked the oil pressure sensor by jumping out and seeing if the compressor kept running. Compressor ran fine with it jumped out. No issues found on compressor. Call complete checked out with manager Victoria | Compressors/Motors | Compressors/Motors | 0.99858
John DiCecco 11-7-23 Travel 0515 Arrive 0545 Depart 1345 Travel 1430 Checkin Taola Arrived and checked in to service channel. RTU12 SGA120H4MS1G 5608G14026 Asset # 038831 Ckt 2 flat. Recovered ckt 1. Onsite decision was made to use virgin refrigerant. Removed old coil and filter driers. Craned new coil onto roof and craned old coil down. Removed bracket and mounting system from coil and installed on new. Replaced filter driers. Pressure Tested both Ckts at 150psi nitrogen and tracer 410a for 30 mins. Bubble checked welds and leak checked entire system. Evacuated both circuits after passing pressure test. Evacuated both to sub500 microns. Charged ckt1 with 25# R-410A and charged ckt2 with 21# 8 oz. (Rest of refrigerant was used for leak check). Started system and noted one condenser fan motor not spinning, one spinning backwards, and one spinning correctly. Found all three condenser fan motor capacitors to be failed. Replaced all three 10uf capacitors with truck stock. System function restored. Call complete. | Capital Replacement | Compressors/Motors | 0.97025
7/21/2023 4:31:29 PM Canadas Garcia, Yelson -0001 I came and checked in with the store manager and checked the BS11A and BS11B system and it was found that the evaporator coil was frozen, so it was defrosted by means of hot water and it remains working under observation since LCD is offline so you have to change the program. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99846
8/17 Tech William Placed in Service Channel Turned freezer back on and observed it come down to temp. Verified more info on hinge that is needed for proper door closing. Ordering Parts from United Refrigeration 8/14 Tech William Placed in Service Channel I replaced a fan motor on a self contained case. I had to source a motor locally so I had to go to several parts houses. I assisted Kody with troubleshooting and diagnosing the neighboring self contained case. We check electrical connections, safety switches, refrigerant levels and pressures. We determined that the case will need a new compressor. Kody is ordering one. 11/17/2023 4:09:07 PM Hendricks, William -0004 I arrived and checked in with the curbside manager. We removed the hinges from the old freezer door. We disconnected the heating wire from the old door. We prepared the new door for installation. We removed the old door and placed the new door on hinges so that freezer would not lose temp during installation process. We installed new top hinge. We adjusted the tensioner so that new door will now close properly without having to be manually shut every time. The door now opens and closes properly. We informed the manager that a new sticker will have to be printed for the new door. The old sticker was too old and fragile to remove intact. We checked out with the manager. 11/20/2023 5:33:36 AM Stark, Keith -0005 Helped another tech replace glass door. We adjusted the torque rod. Door is now opening and closing properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99583
This call is a duplicate of Customer po#251682749 | Nuisance Calls | Nuisance Calls | 0.99825
8/4/2023 8:11:04 AM Simon, Devin -0001 Emailed time 8/4/2023 9:18:35 AM Allemand, Tikie -0002 Came out and found that the roll up door had been hit and was stuck half way. We had to reprogram the door and then made sure it was full operational afterwards | Damage by Customer | Damage by Customer | 0.98101
Completed arrived and talked to manager. Took sizes of broken parts. Picked up new parts. Fixed both drains. One on C7 and one on C6. Let manager know the repair was completed. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99732
8/16/2023 5:25:49 AM Delgado, Jesus -0001 Check in with manager Sean on arrival rack a satellite compressor S3 intermittently going into failure due to current sensing relay board not sending correct output voltage remove board and replace with OEM part install then re-address with same address as existing board spoke with Zack from Home Office was told compressor is now showing amp draw and is at normal. | Compressors/Motors | Compressors/Motors | 0.99864
ST:13:00-14:30 MTB -Arrived checked in with manager. -Gained access to motor room -Found MTB Discharge 264.0, suction pressure 34.5 -Receiver level 20.6% -Took full trash out and replaced the bag. -Checked all CFMs all operational -VFD is in bypass to help with high head pressure. -Checked all safety’s on compressors no issues all safety’s working properly at this time. | Compressors/Motors | Compressors/Motors | 0.98395
Checked in with manager Nate. Located WIF bakery. A08. Found emergency pull down was pulled. Rolled it back up. Tried to closed. Door was still having issues on closing. Found that the Service Cycles was blinking. Read into manual and needed to be reset since it reached its limit. Reset parameters. Verified door opens and closes. Monitored and tested a few times before departure. Checked out with manager Nate. | Non-Mechanical Door Repairs | Damage by Customer | 0.5774
Andrew Debeaulieau 8/4/23 Arrival 1545 Departure 1830 Kysor-Warren OIV5V14-03UN 0809001758 Found txv has high superheat cause inefficiency in cooling. Pumped down system and cleaned txv screen. Return case to service. Call complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99772
Make: KYSOR/Warren Model: TD340-092-VC-4-FHSLX-B Serial: 1112000168 Unit: Rack B & BS -upon arrival the rack was at suction set point. B was at 35 and BS was at 44. -the rack was running at suction set point and the cases were all at temp. I then checked the entire system to see what could have caused the alarm. -this was cases from the rack being down. Not sure what caused to rack to go down but I checked the condenser, compressors and refrigeration and everything checked normal. -this system was also monitored for abnormal activity but nothing was found. No other issues system operational. | Nuisance Calls | Nuisance Calls | 0.9977
Assisted Alan on this call , we began to bringing all the stuff in with the scissor lift , after we had everything in place we then grabbed hot water , brought it to the walk-in and began spraying hot water . We got big buckets under the coils to prevent flooding the walk-in , there was water dropping into the floor so I grabbed a mob and began moping while Alan was de icing coil. After everything was completed and de iced we then mopped the whole walk-in where the water splashed. Walk-in got cleaned . Took everything back together and it’s place and checked out with mark. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99852
0100-1400 4 hours reg time Arrived on site with new gasket and heat tape, new door handles for inside of door and outside, replaced damaged handles both functioning properly, replaced damaged gasket and heat tape, found that door has been hit with fork lift and bent so door wont close properly, talked with manager Matt and door needs replaced. Completing work on another PO. Will submit a quote to replace entire door | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9965
Bs10 leaking water / Please provide the case label number: Bs10 REFRIGERATION (FROZEN, COOLERS, DAIRY ETC.) / Refrigeration / Walk In -Cooler / Water Leak / Name: Greg Vallejos -gdvalle.s06549 / Phone Number: 719-584-3028 / Tag ID: Medium TempB-1-Club Pickup-6549-52416 / Brand: Other / Model Number: null / Serial Number: 4755-3930-01 / Tag ID: 0052416 / Scheduled date: July 28, 202311:37 AM 7/28/2023 3:35:26 AM Gary, Raymond -0001 7/27/23 Ray Gary Was onsite and Greg asked me if I would look at his POS cooler It’s leaking water I cleared the drain with Nitrogen It wasn’t draining like I prefer it to be I went further in my diagnostics and found the main drain line plugged So I cleared that drain with a push pull application Got that cleared and ran water thru the coil and drain line It was moving the water like it should So I cleaned up the mess I made and advised Greg all was good Also the coil was dirty so I used nitrogen to clean the coil THIS JOB IS COMPLETED | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99825
8/18/2023 6:32:50 PM Denison, Carter -0001 Time in 0915 Checked in with manager Got roof hatch open Inspected rack A for leaks with leak detector No leaks on found on roof Locked up roof Inspected cases/walk ins for leaks with leak detector No leaks found in store Checked out with manager 8/24/2023 9:33:00 PM Maldonado, Chris -0002 Start time-2245 End time-2330 complete checked in with manager Aldo Trejo found fan leaking in HMS room drain was clogged, got co2 to cleared drain clean up water from floor checked out with manager Aldo Trejo | Nuisance Calls | Case Cleaning/Deicing | 0.99829
8/22/2023 12:37:03 PM Stuart, Christopher -0001 Time in: 1045 Time Out: 1330 CS10a Service Meat Case High Temp (Home Office Call) Hussmann (CS10a) M# Q3-M/FV-EP-8-R S# 971936 Located CS10a case. Case temp reading 56 at Novar controller and confirmed at case thermometer. Staff still had product in the case. Asked staff to move product. Removed deck pans to access the coil, and the coil had a large amount of thick frost build up(not so much solid ice). Closed off the hand valves to each coil, and de-iced entire case with hot water. Let the coils dry off for about 20 minutes and then opened the hand valves back up. Case temp dropped down to 26 after about 10 minutes. LT-SC1 IC DRS high temping (Home Office Alarm) Hussmann (CPU Freezer) M# RFLN3 S# MY18E041362 R-448a Located curbside pick-up freezer case temp reading 9 on arrival, but staff said that it’s high because of high traffic and the freezer is right next to the exit door. I cleaned the condenser coil, it was caked with dust. Suction pressure @ 24 psi, sight glass solid column, entire case has strong airflow and the coil is not iced up. Monitored the case for awhile and watched it hit sub-zero temps. Jobs Complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
Travel Time 1100 Time in 1130 Time out 1330 Arrived on site checked in mod CARLOS and service Chanel. Proceed to Pharmacy tempnat 71 degrees registers little dirty. Got roof access found rtu20 supply 52 degrees filters just replaced 6-24-23. Went track to Pharmacy got ladder and cleaned all 4 supply registers. Just alittle dusty . No issues with ac and filters good normal lint on registers after yrs of not cleaning. Checked out mod CARLOS and service channel. JOB COMPLETE | Misc. Billable Repairs and Service Calls | Nuisance Calls | 0.90419
7/19/2023 10:28:32 AM Lopez, Miguel -0003 Completed Assisted tech with scissor lift & work order. clean dust per manager request 7/19/2023 11:44:34 AM Jennings, Jeromy -0001 Job completed Adjusted the bottom of the freezer door with the bottom toe kick plate and also adjusted the top track to close the gap on the opening side | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99678
07/17/23 Mario. A Sam 4824 W 230714-0222 F/U Arrived at parts house for CFM in stock, needed fan blade for CFM motor, drove an arrived onsite removed fan blade drove back to parts house, motors will be available follow day, f/u to return next day for repairs F/U | Compressors/Motors | Compressors/Motors | 0.99823
Complete. Assessed door adjusted both top and bottom brackets on door. Had to make several adjustments. Door working properly. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9972
7/26/2023 6:24:40 PM Emmer, Bob -0001 7/26/2023 Bob and Glenn Bakery walk in freezer LTA-6 warehouse side door. Both sides of door gaskets are damaged and torn. Also left side end of door splitting apart. Removed all damaged door gasket and installed new gasket retainer and foam cell filler inside gaskets. Also repaired door with new angle metal. And adjusted door floor stay rollers.Check all operations all good door now working properly and sealing properly job complete. 7/26/2023 7:31:25 PM Alexander Sr, Glenn -0002 07/26/2023-Glenn Sr. and Bob E. Upon arrival checked in with manager and Service Chammel. Proceeded to Bakery freezer door. Assisted Bob on installing door gasket and foam filler. See Bobs notes. Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99707
8/21/2023 3:05:12 PM CERDA, JOSE -0001 Found 5 door gaskets wearing not sealing, found 1 door tensioner sping snapped, found 6 door holders missing or bent, found screws and nuts missing to door holders, found 2 cooler gaskets breaking, found doors tensioner loose doors not closing. Found evaperater iced up, ice on back walls and tension pins stripped. Adjusted all door tensioner doors now close. Removed ice from frame and gaskets. Forced defrost to deice coil. Pushed gaskets back in that were pulled out. MOD to turn case off tonight with doors open over night to deice coil Case at -3. 9/18/2023 8:12:52 PM CERDA, JOSE -0002 Returned to store with parts. Replaced door holders, replaced door tensioners, replaced door gaskets and, replaced missing hardware. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.98798
Incomplete, waiting on parts. Arrived onsite, checked in with manager. Assisted tech on site with LTA4&5 work order. Assisted tech with scissor lift to adjust freezer door. Inspected issue. Door in need of new Gasket. Adjusted track to resolve, Door overall falling apart from forklift damage. New door recommendation. Emailed willie measurements and serial number. 76inx 108in | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99733
8/16/2023 6:38:55 PM Gonzalez, Alan -0001 Checked in with Emilio Let him know there is a compressor that is off in rack A. let him know I need the rack house open so I can go in and check it out. Once I was at rack A I checked the oil pressure for the compressor and tried resetting them to see if it would turn on but it did not. Checked suction and discharge pressures and they were good. Checked the controller to make sure it was calling that compressor to turn on and it was. I removed the contactor cover to see if the contact points were okay. Noticed they were pitted and not in good condition. Contactor is bad, went to the parts store and got a new contactor and auxiliary. Arrived back on site and replaced contactor and compressor 5 is still not turning on. Checked voltage for all of the connections going to compressor 5 and everything was receiving power. I noticed on the board that compressor 5 output did not have anything hooked up to it. I checked voltage coming from that output and did not get any power coming out. I turned the switch from auto to on one by one to see what was controlling each switch. I found that output #10 when I turned it to the on position it would turn on compressor #5 I called Sam’s tech support so I could speak with Novar. They were not able to verify that output 10 on the board was controlling compressor 5 and they were not able to help me out. Everything is running as it should as of now and pressures are good. Checked out with Hamid Job complete Rack a R-422d Discharge psi 245 Suction psi 48 Reciever level 25 | Compressors/Motors | Compressors/Motors | 0.99848
Travel: 10:00-12:00 Onsite: 12:00-14:30 Onsite OT: 14:30-15:00 Sn# Sam’s Club 6624 Sc# 230727-0159 Po# 251956177 System: RCU Cafe Cooler “Leak detection alarm” Upon arrival checked in with MOD and ServiceChannel -Leak detection alarm and siren going off on RTC-Cooler on Cafe -Used electronic Leak detector in cafe and cafe cooler. No leaks detected -Located leak detector module in Cafe Cooler -Leak detector module looked as though it had been hit off the wall -There was no green power light on the face of module upon arrival -Reconnected face to module and green power indicator light turned on -Verified module face was working properly by swapping with a known functioning module -Module working properly -Reset leak detection alarm in electrical room -All zones enabled -Informed MOD of work performed and obtained a signature before my departure. Job complete | Damage by Customer | Misc. Billable Repairs and Service Calls | 0.76043
8/4/2023 5:05:01 AM Ried, Nicholas -0001 Parts needed. Incomplete. Please order. Checked both bakery freezer doors. Recorded information needed for expediter to order safety strap assembly’s for both bakery freezer doors. Please see attached photos and information below. Roll Seal Door RS500 Model 6421-2281 Serial number 0004219 Need safety strap assembly only 2 techs 4 hours each Roll Seal Door RS500 Model 6640-12112 Serial number 00003600 Need safety strap assembly only 2 techs 4 hours each 8/30/2023 4:12:19 PM Moran, Greg -0003 Completed arrived met with manager. Replaced emergency straps on bakery freezer and cooler roll up doors. 8/31/2023 8:46:36 AM Cochran, Lila -0002 Complete assisted Greg Moran installing pull seal door safety straps. Accidentally got managers signature on the wrong ticket. Added screen shot in attachments | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99672
7/19/2023 9:34:18 PM Manaog, Efren -0001 Arrive onsite and checked in with service channel and MOD Judy. LT CU2 Cafe Freezer -Found evaporator ice up front and back -De iced evaporator coil -Checked condenser and has high discharge pressure -No water outlet nearby. Used nitrogen to blew out condenser. Discharge pressure went down to 275psi with suction of 25psi R404a -Monitor the box. Products are a foot away from the discharge air and it prohibits the air flow. Removed product from top shelve and temperature went down to -1f -Locate manager and talked to MOD Judy and showed her what I found -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
7/15/2023 12:31:53 AM Medina, Alexis -0001 7/14/23 Sam’s club 6628 Controller MTC & LTA issues. Alex Medina arrived on site , checked in on IVR and MOD Alvind. Call was for MTC rack showing as LTA and vise versa. Headed to machine room. Checked controllers on rack. MTB controller showing proper circuits and info as it should for medium temp. LTA controller showing proper circuits and info as it should for low temp. Power cycled each controller including the building controller. Contacted home office and confirmed all racks communicating. Per home office, all racks indicating proper levels and info on their end. No issues on their end. Tested each controller by putting multiple circuits through a defrost to confirmed proper ops and communicating. All ops okay. Racks at suction and maintaining. Informed MOD. CALL COMPLETE. | Nuisance Calls | Nuisance Calls | 0.99095
7/21/2023 3:37:36 PM Robak, Anthony -0001 Anthony Robak Checked in with Fernando Went to rack c to check monitor for club pickup case LT-SCa. IC Found case at -4.8 degrees Found case C6 at 31 degrees Called home office and confirmed case C6 was at 49 degrees during defrost at time of call Both cases at temp Will return in am to check ops on case LT-SCa Staff is gone for the night follow up 7/21/2023 4:30:31 PM Robak, Anthony -0002 Anthony Robak Checked in with MOD Went to front of club pickup for LT-SCa Found case at 1 degree even with door open Case has good airflow Due to high traffic this case struggles to get down to setpoint Management aware Case at 0 degrees at time of departure complete | Nuisance Calls | Nuisance Calls | 0.99571
GP#230728-0138 0700-1000 RT Checked in with store manager. Working on cafe rtu not blowing air. Located RTU #14 as cafe unit. Found unit tripped on alarm 32 freezestat open. Refrigerant pressures below freezing point. Filter inside return register installed very dirty. Removed filter. Filters installed on unit replaced on 6/1/23. Refrigerant pressures raised after removing filter. Unit working correctly. Job complete. Lennox #14 M/N: SGCO6OH4BH1G S/N:5614B00888d | Nuisance Calls | Misc. Billable Repairs and Service Calls | 0.99107
Found all compressors on rack b running. Discharge pressure is running at 345. I shutdown the rack and condenser. I washed out the condenser coils. Head pressure is now running at 265psi. All cases are now down to temperature. | Compressors/Motors | Compressors/Motors | 0.99836
10/19 Checked in with manager. Performed follow up leak search on rack B. Checked motor room, condenser and sales floor for any potential leaks. Receiver level is currently at 50%. There were no leaks found on any areas for rack B. Will not haft to add any refrigerant to the rack. While checking for leaks in the motor room I found that compressor 4 on rack B was in a motor protection trip on the coresense protector for the compressor. I was able to trouble shoot and find that the winding’s resistance are reading high at 0.85 ohms and the Compressor windings are only rated for 0.35 ohms +/-7% per the manufacturer. Ohm readings on the windings are well out of the 7% threshold given by the manufacturer. Tagged out the compressor and will need put in a quote to replace it due to high winding resistance. Attached is the data tag for the rack, data tag of compressor, coresense module, and Adjustable oil regulator that will need to be ordered and replaced, including 1 3pole/50amp/208-240v contactor. Also attached is a screenshot of the line to line rated winding resistance and the current winding resistance reading. Verified all electrical connections were tight and secure. | Compressors/Motors | Compressors/Motors | 0.99851
8/7/2023 1:40:14 PM Monsivaiz, Armando -0001 WO/COMPLETE..Drove to site logged in with service channel located curb side. Inspected all doors on coolers an freezer in curb side. Adjusted couple doors but when finished associate said they where having issues with emergency exit door. I had to confirm with our service manager he then mentioned we do not work on emergency exit doors. | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.9964
Job completed. Informed management why I was on site. Located both freezers on site and looked into the ice building up. Found the freezer doors have metal rails that are welded onto the berms that surround the inside of the door. This are in the way of the strip curtains and not allowing them to lay flush against each other. This cause the air to enter the box when ever the door open. This will cause ice over time because you will build sweat on the metal frame. The right hand freezer(LTA3&4) also has a small gap on the bottom of the door. This is from missing concrete. Unless we cut that welded metal piece and level out the concrete and keep the employees from working with the doors open this will be a reoccurring issue. I was able to clear off the ice for now. Heaters on both doors are working properly as well. | Non-Mechanical Door Repairs | Case Cleaning/Deicing | 0.98972
8/3/2023 Jones, Makayla -0001 Used scissor lift to access evaporator in meat market. Will need to return with new motor and deice coils. Floor drains are clogged right now in meat department. Do not want to deice coils and flood back area. 08/2 Checked in with manager. Was told I need a certain tool for packing nut leak. Went to united to get one. Waited for the scissor lift to be finished with when they were working on sprinklers. Washed both coils. Changed fan motor and blade. Adjusted superheat. Cleaned up. Job is complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9974
Arrived on site and checked in with manager mark. Told to look for devin in charge of the meat department. Went to devin. Devin said there was a leak in the evaporator drain line above the meat cutter but it hasn’t happened in a week. Went to the meat prep room and looked at the evaporator fans were off in defrost. Waited to see if there was any leak on the unit since it was in defrost. Waited for the defrost to end without any leaks. Grabbed the ladder from the van and set it up underneath the evaporator coil and drain line. Grabbed a water measuring cup and filled cup up three times with water, pouring it to drain pan to recreate leak. No leaking. Repeated process again with another three cups of water. No leaking. Brought ladder out to van and checked out with manager mark. Call complete Model WK15GAC Serial TO8M03816 Heatcraft No asset tag or circuit indicator | Nuisance Calls | Case Cleaning/Deicing | 0.99802
8-3-23 Paul Z / fan making noise Kyser warn S# C19m00156 Checked in with Thomas removed product from case found case is full of water and fan blade is slapping water cleared drain with co2 debris was released from case case is clear of water Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99843
7/31/2023 6:30:06 PM Maldonado, Chris -0001 Start time-1400 End time-1945 complete check in with manager Ruben MTB23 A,B, and C coils and iced up put coils in defrost and de-iced coils cleaned up ice and water on the ground call is related to #248675516 checked out with manager Sammy Wonn | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99858
8/19/2023 3:26:55 PM Toomer, Collin -0001 OT TT:16:00-16:45 OT:16:45-17:30 Arrived checked in with Kaye Located freezer in curb pick up, MODEL: FX5SL -O3RUN SERIAL NUMBER: C17H00393 Upon arrival freezer at -4 degrees Checked condenser it’s clean, spoke with curb side manager she said that the manager that sent in the call said it wasn’t at temp and said def on screen. Unit was in defrost when she seen temp and called this in no issue found freezer is working Spoke with manger Kaye about it. Checked out with manager Job complete. | Nuisance Calls | Nuisance Calls | 0.93796
Arrive onsite and checked in with service channel and MOD Anderson MTC12 -All case high temp. Good air flow and no evaporator ice up -Suction/Discharge pressure reached set point pressure -Went up to the roof and receiver level at 60% confirmed this using torch -Compressor 2;3;&4 are toggle off. Compressors are in order according to previous tech. Waiting for compressor to come in -Request to removed products. Checked case filter drier and none are plug. -Case are cooling down and struggles after it come out of defrost. -Locate manager and talked to MOD Anderson and showed him what I did -Job complete. | Compressors/Motors | Compressors/Motors | 0.8357
Cho and I came and checked in with the store manager and we found that there were two evaporators turned off, one from the A8 system and the other from the A9 system, so we checked them and found that the evaporator of the A8 system was bad, the switch, so we The problem was corrected and it is still working, in the A9 system the transformer was burned, so the original was ordered but one was put in while the original arrives, so it remains pending for the part to arrive and to come and change it. | Capital Replacement | Misc. Billable Repairs and Service Calls | 0.96385
7/24/2023 3:46:44 PM Alcaraz, Jose -0001 TT 1500-1600 Time in 1600 Time out 1730 Call complete Arrived log into service channel and check in with manager for LTA comp A5 -found compressor A5 off on high suction -got compressor back online -cleaned condenser -one fan is out and has been ordered -checked with dispatch fan has been delivered -will return tomorrow to remove and replace condenser motor on WO 230618-0178 | Compressors/Motors | Compressors/Motors | 0.99852
0900-0930 travel 0930-1130 Called for rack B compressor offline Met with manager Jen Inspected rack and found compressor B2 offline Checked and found compressor off on oil fail. Verified comp not full of liquid, restarted and checked ops. 45psi Net oil pressure. All ops check good | Compressors/Motors | Compressors/Motors | 0.99852
Deice dairy cooler Checked in with Mark Let him know we were here to deice the evaporators in the dairy coolers units C8-C13. Asked if we could have some of the pallets moved from the middle of the cooler. He said he will send someone to move them for us. Got the scissor lift and moved them in the dairy cooler. Went to my van and got my trash can and sump pump with hoses. Set up the hoses and went to get hot water in my trash can. Once everything was set up we checked each evaporator to see which ones needed to be Deiced. Evaporator C8, C9 and C12 had ice on both sides of the unit. Started by deicing unit C12 first, as we were spraying water on the coils there was water dripping on the floor so we went to get a big container so the water would fall in there. As water fell in the container some would still splash on the floor so we went to get a mop and bucket. As one of us sprayed water in the ice the other one would mop up the water that would get on the floor so customers would t slip with the water. Once done with that unit we moved over to C8 and did the same thing. Unit C9 was the worse one with a lot of ice on both sides. As we Deiced the evaporators we had to keep going for more hot water so we can clear out all of the ice. After melting all of the ice we moved out the scissor lift and cleaned up all of the puddled water on the floor. Cleaned up the area and took our equipment back to the van. Checked out with Mark Let him know what we did. Job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9979
7/26/2023 3:34:08 PM Brooks, Byron -0001 Time in: 1300 Time out: 1330 went inside sams club Located case MTB19-a Product blocking means of service Removed product Disassembled unit No water in unit only from under Reassembled case Acorn system not working right Informed manager to call acorn Checked out with MOD Call complete | Nuisance Calls | Nuisance Calls | 0.95344
8/16/2023 De la Cruz, Adrian -0002 8-15-2023 Adrian De La Cruz Jr GP# -230815-0298 PO# -253785111 Checked in with store manger. Spoke to the store managers to see the problems they were having. Located the walk in cooler I saw the concerns the store managers had about the walk in cooler. It was different shades of lights in there. The father you went down the walk in the more dim the lights got. I assisted my Lead tech for the rest of the job. Discovered we need to order a Balice control box. -follow up needed for parts -job complete 8/16/2023 Mares, Jeremiah -0001 8/16/2023 Jerry Mares GP# 230815-0298 Arrived onsite and checked in with Management. Located POS Cooler to check lighting issues club is having. Management said how there was 2 bright lights in the entrance of the cooler then goes dim towards the back. The lights were dirty, one light was completely out and another is flickering. Gained access to the scissor lift to get up to the lighting and checked each light. Cleaned off plastic covers and verified proper operation. Need to replace 2 LED drivers on 2 lights. Will order parts come back and replace. Pending Parts Philips LED Driver LED-INTA-1000C-60-DB 10/2/2023 Mares, Jeremiah -0003 10/2/2023 Jerry Mares GP# 230815-0298 0700-0800 RT Picked up parts at shop. Will head down to store and install in the morning. 10/4/2023 De la Cruz, Adrian -0005 10-4-2023 Adrian De La Cruz Jr GP# -230815-0298 PO# -253785111 Checked in with store manger in the morning. Came to replace LED drivers with my fellow tech on the POS coolers. I was his spotter We verified proper operation. -Job complete | Misc. Billable Repairs and Service Calls | Misc. Billable Repairs and Service Calls | 0.99686
7/25/2023 2:31:01 PM Eddy, Bill -0001 TSn: SC# 6624 Sc# 230724-0467 Po# 251692338 System: RTU 17-High Space Temp UPON ARRIVAL CHECKED IN WITH MOD AND SERVICE CHANNEL APP -RTU 17 ZONE TEMP WAS 81 -EVAPORATOR COIL AND COMPRESSOR WERE PARTIALLY ICED UP, DUE TO LOOSE BELT -ALLOWED RUN TIME TO DE-ICE COIL -PICKED UP 100FT OF WATER HOSE TO REACH CONDENSER COIL -CLEANED CONDENSER COIL: VERY DIRTY -TIGHTENED BELT AND RECORDED SPLIT -SUPPLY AT 56 -RETURN AT 82 -INFORMED MOD OF WORK PERFORMED AND OBTAINED A SIGNATURE BEFORE MY DEPARTURE. JOB COMPLETE. 7/25/2023 5:05:04 PM Brooks, Brandon -0002 Sn# Sam’s Club 6624 Sc# 230724-0467 Po# 251692338 System: RTU 17 -High Space Temp UPON ARRIVAL CHECKED IN WITH MOD AND SERVICE CHANNEL APP -RTU 17 ZONE TEMP WAS 81 -EVAPORATOR COIL AND COMPRESSOR WERE PARTIALLY ICED UP, DUE TO LOOSE BELT -ALLOWED RUN TIME TO DE-ICE COIL -PICKED UP 100FT OF WATER HOSE TO REACH CONDENSER COIL -CLEANED CONDENSER COIL: VERY DIRTY -TIGHTENED BELT AND RECORDED SPLIT -SUPPLY AT 56 -RETURN AT 82 -INFORMED MOD OF WORK PERFORMED AND OBTAINED A SIGNATURE BEFORE MY DEPARTURE. JOB COMPLETE. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99772
Arrive onsite and checked in with service channel and MOD Ashton. MOD Ashton showed me all the case is running on negative temperature. Meat SD cooler MTA 6.3 6.4 6.5 MTA 7.1 A B C MTA 7.2 A B C MTA 8.1 A B C MTA 8.2 A B C MTA 8.3 A B C -Went to Rack house and all compressors are online. Receiver level at 20% and no alarm. Notice the Rack monitor is offline -Called Sam’s Club HO and Rack A is in loss comm -Restore communication. Called Sam’s Club HO and Rack A is back in communication -Checked each case for air flow and found MTA 6.3 no air flow. Removed all panels and de iced the coil using trash can and water pump -Monitor all case and it reached target temperature of 22f. None of the case went down to negative temperature -Run defrost to all case and temperature reached set point and controller turned off the refrigeration -Locate manager and talked to MOD Veronica. Showed her all the cases that are holding the temperature desired -Job complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.9982
Assisted Adrian on call Checked in with store manger Amy Rhea. Located freezer door handle that needed to be replaced because it was damaged. We took off the damaged door handle parts and replaced them with the new door handle parts that we got ordered in back home in El Paso. Me and my partner coordinated taking it apart and putting it back together properly on the freezer door. When we were done we tested the new installed freezer door handle to make sure it was opening and closing correctly. -Job complete | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.997
Multiple failures may be due to power outage, power cycling, controllers, Check in with management on arrival call digital assets/Novar tech-support. Multiple times call kept getting disconnected. Novar, Tech Support configured staging of compressors on rack A secondary compressor s3 not staging on due to CT board Not reading amp draw went through multiple troubleshooting procedures with tech-support determine CT board needs to be replaced. Board not Allowing suction pressure to maintain. Explain to management will return with new board. This call is not completed. | Misc. Billable Repairs and Service Calls | Compressors/Motors | 0.9983
Completed Checked in with manger on site went to rack c found compressor 2 off reset high pressure switch compressor came straight on then inspected compressor checked oil rack was full on oil and compressor was too then called Digital asset an made sure it was running good they said it was good no other issue found | Compressors/Motors | Compressors/Motors | 0.99857
7/25/2023 7:22:47 AM Ramirez, Julio -0001 Job is complete Arrived at store. Checked in with manager. Located case MTB-10e on sales floor. One side of case had no airflow. Went ahead and cleared product to remove bottom panels. Once removed saw that drain was clogged and case had standing water. Also due to water one of the fan went out. Went ahead and cleared drain clog and made sure it drained to flor drain. isolated old motor and removed and installed new motor. Energized new motor to make sure rotation is good and good airflow on top of case. Checked to make sure case temp dropped and maintained temp. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99795
8/19/23 arrived on site and checked I. With Rosemary the MOD. Went to rack room and verified all compressors are on line and checked case temperature. Went to walk in and verified that cooler was back at temperature. Found MTB-5 evaporator pan knocked loose due to product being lifted too high with forklift causing screw in back to dislodge. Reattached drain pan in correct position. This will complete this work order. | Damage by Customer | Case Cleaning/Deicing | 0.99019
Favian Porrata 07-19-23 Travel 1600 Arrival 1800 Departure 2030 HeatCraft M#DX6XN-08RUN S#C17F00512 Upon arrival checked in with Manager Jeremy. Call was for case for not holding proper temp. Started off by checking airflow and found it to be weak. Began to check evaporator coils and found them to be dirty. Also checked honey combs and baffles. Baffles where clean but honey combs where dirty as well. Talked to manager about pulling hose to clean coils and honeycombs. Got access to water and ran hose on top of cases. Cleaned the evaporator coils and they are now clean. Use water to clean Honeycombs and now also clean. Put cases back together and honeycombs back up. Case is now at temp 34. Checked out with manager Jeremy. Call complete. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99831
8/9/2023 3:08:28 PM Canadas Garcia, Yelson -0002 Cho and I came and checked in with the store manager and we found that there were two evaporators turned off, one from the A8 system and the other from the A9 system, so we checked them and found that the evaporator of the A8 system was bad, the switch, so we The problem was corrected and it is still working, in the A9 system the transformer was burned, so the original was ordered but one was put in while the original arrives, so it remains pending for the part to arrive and to come and change it. 9/6/2023 3:49:34 PM Ried, Nicholas -0003 Completed. Checked in with management. Moved pallets in freezer. Accessed evaporator with scissor lift. Removed temporary transformer and installed the proper one. Waited for escort for the scissor lift. Function tested equipment. No further issues. Waited for proper temperatures to be reached. | Capital Replacement | Misc. Billable Repairs and Service Calls | 0.94808
Found compressor 3 tripped on high head pressure. Rack discharge got up to 345psi today and pressure control was set at 300. Raised pressure control to 375psi. Found 1 fan motor now spinning. Started trouble shooting and found the contractor bad. Replaced contractor with one that was on site already. All motors are now currently running and head pressure is down to 295psi. Condensers on both racks are in rough shape, I recommend changing out condensers on both Rack A and B. Rack is currently back up and running. | Compressors/Motors | Compressors/Motors | 0.99829
8/3/2023 9:34:59 PM CERDA, JOSE -0001 Found Case reading 98° and 67° Found 2 cases coil iced up Found cases not defrosting Deiced coil with hot water Replaced sensor with one Found in rack house Temp now reads Cases came down to temp Now goes into defrost | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99855
7/21/2023 12:44:46 PM Fenton, Typhan -0001 Make: hill Phoenix Model: O5DM8 Serial: 1309422 Unit: 4.2 -upon arrival case was at 61f with no air flow and all the products were pulled. -disassembled case and found drain plugged and one fan motor was out. I cleared drain line then washed drain pan and flushed drain line. Evaporator fan was replaced also. -reassembled unit and started it back up. Wait for case to pull down to temp. Case pulls down to temp. No other issues system operational. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99823
8/2/2023 3:01:33 PM De La Torre, Emilio -0001 08/2/23 EDLT WIF A4.2 and A5.2 Checked in with mod upon arrival My Corrigo isn’t loading up having issues with my app or data Went to freezer temps were at 8 and 9 on both the freezers walked inside the freezer everything was running no ice build up all fans were running Checked pressures all were good to Liquid level was good Watched the freezer for awhile and seen temps drop and go back up when people would open the doors and back door Checked graph logs and matched it to see if it would drop to temps and they do when the store is closed The temps will rise back up when they stock up and let the doors close Freezer usually takes a while to drop back down but the store opens and due to the amount of people that open the doors the temps will rise and drop Informed mod about it Complete | Nuisance Calls | Nuisance Calls | 0.99783
7/28/23 TH Time in: 14:30 Time out: 15:00 Refrigerator (Break Room) True MN: T-23-HC SN: 10529373 Arrived on site and checked in with Service channel and MOD(Hilda). This called is duplicated call. Reference PO# 250963827. Informed and checked out with MOD(Hilda) and Service channel. Job finished | Nuisance Calls | Nuisance Calls | 0.99841
8/5/2023 7:55:27 PM Ochoa, Alfredo -0001 080523 Alfredo Cake case warm System MTA16/MTA9 Tyler Mod:N6DL12 Ser:5158261 TT/OT-1630-1730 OT-1730-1930 Arrived at location and checked in with service channel and store manager. Bakery manager not on site and employee called manager and stated cake cases warm earlier in the day. Located bakery cases and asked manager to please move a couple of sections from both cake cases to check operations. Found all fans operating for both cases and no ice build up. Found one case with standing water due to debris and gunk blocking water flow. Both cases at temp. Cleared gunk blocking drain and used water to clear remainder of gunk and now water draining properly. Checked suction pressure for both cases and both at 55psi with a discharge air of 33°. Informed employee he was able to put all product back in cases. Call completed. | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99813
8/17/2023 6:07:32 PM Hooper, Zackery -0001 8/17 Checked in with manager. Upon arrival I found that all of rack MTC was down due to com loss and network failure. I spent 3-4 hours on the phone with sams club/novar reprogramming controls and re-syncing all circuits that were out on com loss. Also found that the defrost schedule was set on all circuits on mtc to 6 times a day with terminations temps set to 55 degrees and defrost length was set at 40 minutes for each defrost. Had sams club program defrost to 4 times a day for 30 minutes with a defrost termination temp at 45 degrees. Was able to get rack back up and running and made sure all circuits were reaching set-points. Once all compressor came back on I was having issues with liquid flood-back to the compressors. Due to rack being down for so long it caused liquid to stack in the oil reservoir causing compressors to go out on oil failure. Got on the phone with David G. To get some insight on getting liquid out of oil reservoir. He had me isolate compressor 3 which was the main compressor having the most liquid flood back. I allowed comp 14 to cycle refrigerant through the system and was eventually able to remove the liquid from oil reservoir and out of compressors. Opened valves back up on comp 3 and allowed system to run for an hour to ensure there would not be anymore oil failures or issues with high temps at the circuits. David wants me to put in a follow up for him and myself to return this following Monday 8/21 to go back over rack and system operations. 8/21/2023 11:33:55 AM Garreans, David -0002 TTST 0800-0915 Time in 0915 Time out 1330 I had shut down sub cooler because it was flooding out rack causing oil failures. I came back and provided assistance in getting sub cooler working again. Temperature sensors for sub cooler were reading incorrectly, replaced all sensors on sub cooler controller. Turned sub cooler on and it is now providing sub cooling on the liquid going out to circuits. Monitored to make sure it maintained proper super heat and did not over feed and flood out rack again. Compressor 2 and 3 are locked up on LRA, compressors will be changed in one of the multiple tickets open for this issue. | Compressors/Motors | Compressors/Motors | 0.99853
1130-1200 labor Arrived on site and checked in with manager Sandra Was told by an employee that someone from another company was just here working on prep table and they’re ordering gaskets for the unit. Spoke to manager and she wasn’t aware of someone else working on it. She told me to not check it out Checked out with manager Liliana | Nuisance Calls | Non-Mechanical Door Repairs | 0.98984
traveled to store. found walk in Cafe freezer at 37 degrees. gained access to roof and found unit at 450 psi and opening and closing on its high pressure controll. We cleaned out condenser and head pressure still super high. we ended up pulling out 12 oz. of gas and got head pressure down to ambient plus 30. unit now back online and working. the box is now at 10 degrees and dropping. I will leave call open and check on it after the weekend. if everything maintains I will close call out Monday. | Compressors/Motors | Misc. Billable Repairs and Service Calls | 0.99455
Arrived onsite checked in with mod gained access to rack house checked the vfd not showing fault on b/bs rack checked compressors and idcm no issue found checked all condenser fan motors and amped motors checked the transducer for discharge I believe it’s a program issue will follow up | Nuisance Calls | Compressors/Motors | 0.99527
7/18/2023 3:02:24 PM Rivera, David -0001 7/18/2023. Checked in found the unit A-03 Had to get lift ,shut system down pulled fan guards off and found plastic in side drain pan and inside of drain line. De iced and got all plastic out cleared drain line and reinstalled fan guards then turn system all on . Job completed | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99857
Cooper Nichols 8/15/23 Arrival 1330 Depart 1500 Call was for suction alarm on rack B Went over all ops and found nothing wrong Everything is operating good at this time No alarms @ arrival and none @ departure | Nuisance Calls | Nuisance Calls | 0.99828
Arrived on site checked in went to motor room and found compressor running checked date on when it came in call had came in when rack went down compressor is running checked out | Compressors/Motors | Compressors/Motors | 0.9986
-While on site inspected coils and verified all clear -defrost ops working and coils de-iced on their own -job complete | Case Cleaning/Deicing | Case Cleaning/Deicing | 0.99807
Replace 3 door gasket due to cuts on gaskets | Non-Mechanical Door Repairs | Non-Mechanical Door Repairs | 0.99656
8/17/2023 9:04:42 AM Becissa, Bachir -0001 Called out to check cases running high temp. Upon arrival found tech had already run the call earlier this morning. Walked store. Everything seems to be working fine. | Nuisance Calls | Nuisance Calls | 0.99795